## Sheet1
Estimate Quantity (only Figures) | Item Detailed Specification Description | Work Type eg. Earth Work, Electrical works.. etc ( upto 200 Characters) | Item Short Description ( upto 100 Characters) | APSS / Morth Cl. Number ( upto 200 Characters) | Rate (INR) ( Upto 2 Decimals ) | UOM ( upto 50 Characters) | Amount (INR) ( Upto 2 Decimals )
20 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevaent standard specifications | 600 | EA | 12000
31 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevaent standard specifications | 2400 | EA | 74400
27.28 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.76x0.76x1.52M with CC mix of ratio 1:3:6 Using form boxes (0.88 Cu.Mt)*31 with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevaent standard specifications | 6579 | M3 | 179475.12
0.96 | ERECTION OF S.S. STRUCTURE: Coping of 0.45x0.45x0.45Mt with 1:8 slope Using form boxes (0.031Cumt.) | Civil work | Coping & Muffing-Iron Pole | As per relevaent standard specifications | 3893 | M3 | 3737.28
31 | Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of poles with two coats of white cement (including cost of paint). | Electrical work | Paint-9.1M PSCC Poles as desc SSR | As per relevaent standard specifications | 485 | EA | 15035
5.5 | Fabrication of 100 X 50mm MS Channel for formation of 11kV and 33kV bays: Fabrication and erection of M.S,Channel 100x50mm for forming of 33KV & 11 KV Bays as per standard specifications to facilitate stringing of bus, erection of LA sets, AB Switches bolts & Nuts etc. including painting with one coats of red oxide and two coats of Aluminium paint. GI bolts&nuts shall be used. | Electrical work | Fabr & Erect-MS Chnl 100x50mm for SS Bay | As per relevaent standard specifications | 6600 | TO | 36300
115 | Erection of 33kV and 11kV Strung Bus with Panther (200Sqmm) ACSR Conductor: Erection of 33kV and 11kV Bus over the Substation structures with 200sqmm Panther ACSR conductor and giving Jumpers to connect the Switch gear by providing the suitable T clamps and round clamps suitable to Post type insulators & Insulators. | Electrical work | Stringing of bus with panther conductor | As per relevaent standard specifications | 327.68 | M | 37683.2
2 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevaent standard specifications | 4500 | EA | 9000
10 | Erection of 11kV AB Switches 800/400 Amps includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevaent standard specifications | 3200 | EA | 32000
3 | Supply & erection of 11 kV 400 A convential single(1/3) phasing AB switches.includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | S&E-400A 11KV ABSwth Conv 1ph(1/3) in SS | As per relevaent standard specifications | 4232 | EA | 12696
2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt). | Electrical work | Hoisting post ins&hrd wr 1panther 33kv | As per relevaent standard specifications | 781 | EA | 1562
4 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Electrical work | Hoisting post ins&hrd wr 1panther 11kv | As per relevaent standard specifications | 507 | EA | 2028
12 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical work | Painting AB switch OP rods with PO red | As per relevaent standard specifications | 142 | EA | 1704
16.46 | Excavation of pit in all types of soils of size 2.2x2.2x0.85Mts.for Construction of Plinths for VCB (33KV & 11 KV ) | Earth work | Excavate-Pit for 33KV VCB | As per relevaent standard specifications | 331 | M3 | 5448.26
22.24 | Providing of Base concreting (2.2x2.2x0.15 Mts) with 1:3:6 Concrete mix. Using form boxes, Providing of Concreting (2x2x1.0mts) with 1:3:6 Cocrete mix. Plastering of the plinth for smooth finishing with 12mm thick 1:3 cement motor and providing two coats white washing for part of the plinth above groung level. | Civil work | Cement concrete with 40MM metal VCB plin | As per relevaent standard specifications | 5160 | M3 | 114758.4
4 | Erection of Switchgear complete for 11 kV VCB includes Assembling the VCB Structures and mounting the VCBs over the already erected foudation including wiring of Breaker Control Panel/CTs, erection of CTs and control pannel providing Jumpers. | Electrical work | Erection of 11kv VCB | As per relevaent standard specifications | 12000 | EA | 48000
2 | Erection of 33KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 33kv LA stn type incl earthing | As per relevaent standard specifications | 880 | SET | 1760
1 | Erection of 11 KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 11kv LA stn type incl earthing | As per relevaent standard specifications | 559 | SET | 559
3 | Erection of 11 KV Lightening Arrestors line type complete including jumpering. | Electrical work | Erect of 11kvLA line type incl earthing | As per relevaent standard specifications | 505 | SET | 1515
1 | Supply of 33kv HG fuse set including providing of jumpers | Electrical work | S-33KV HG Fuse Set excl Ins & Chnl | As per relevaent standard specifications | 6431 | SET | 6431
1 | Erection of 33kv HG fuse set including providing of jumpers | Electrical work | Erect. of 33kv HG Fuseset incl earthing | As per relevaent standard specifications | 1331.81 | SET | 1331.81
1 | Supply of 11kv HG fuse set including providing of jumpers | Electrical work | S-11KV HG Fuse Set | As per relevaent standard specifications | 1733.75 | SET | 1733.75
1 | Erection of 11kv HG fuse set including providing of jumpers | Electrical work | Erect. of 11kv HG Fuseset incl earthing | As per relevaent standard specifications | 740.52 | SET | 740.52
22 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevaent standard specifications | 3486 | EA | 76692
22 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevaent standard specifications | 1234.2 | EA | 27152.4
500 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification.75x8 mm MS flat for Earth mat and connecting to electrodes. | Electrical work | Laying of earth mat,excavation 75x 8mm | As per relevaent standard specifications | 65 | RMT | 32500
950 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification. 50x6 mm MS flat for raisers, double flat shall be run for structure poles raisers & equipment earthing. | Electrical work | Earthing for raisers of SS Flat 50x6 mm. | As per relevaent standard specifications | 41 | RMT | 38950
2 | Providing of double earthing for neutral with flexible copper jumpers of adequate size including arrangement by fixing M.S.Channel 100x50mm. | Electrical work | SupCU Flexi jumper for Power T/F Neutral | As per relevaent standard specifications | 4725 | EA | 9450
4 | Erection of 24 Volts Battery along with Charger on the VCB plinth and giving DC supply to VCB's. | Electrical work | Erect-24V Batery with Chrgr incl grot-SS | As per relevaent standard specifications | 1050 | EA | 4200
600 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable includes excavation of earth and back filling with sand and earth in alternate layers . The cable termination shall be made by providing proper size lugs and shall be identified with colours. | Electrical work | Laying-4 core cable | As per relevaent standard specifications | 15 | RMT | 9000
1 | Erection of 25 KVA Three phase Station Transformer on the Substation Structures and giving jumpers/connections on HT side to the 11kV bus. Belting angle shall be provided both sides of DTR for securing DTR firmly in position. | Electrical work | Erection of Three Phase DTRs | As per relevaent standard specifications | 1139.95 | EA | 1139.95
1 | Supply of AC Panel Board includes: Fixing of 1 No.100A, MCCB, 10kA capacity of any standard make including material cost. Fixing of suitable panel box 3x3x1 with M.S.Sheet of 16 SWG with front door compartments inclusive of material cost & powder coating (with C Channel ). Fabrication of panel Fixing of 96x96mm analog voltmeter with VSS switch Fixing of 20A HRC fuse Fixing of 3 phase supply indicator kwith HRC fuses Supply and fixing of 6 Sqmm copper flexible wire (PVC) Fixing of Stud type TBs for outgoing feeder Fixing of Epoxy bus supports. | Electrical work | Supply of AC Supply panel complete | As per relevaent standard specifications | 42000 | EA | 42000
1 | Supply of DC Panel Board Fixing of suitable panel box of size 6'x6'x1' with M S sheet of 16 SWG with back doors (4'x6') and on front side with provision to fix up bakelite hylam sheet size of 4'x6' including cost of the panel with powder coating. Fixing of best quality of angles for panel. Fixing of C Channelfor panel. Fabrication of control panel including making suitable holes and board Fixing of Stud type TBs for outgoing feeder Fixing of 24V DC pilot lamps of standard make Fixing of healthy trip push buttons with LED lamp Fixing of plain switches for alarm acceptance and for PTR signal Fixing of ON/OFF push buttons Fixing of digital volt meter for 11kV Fixing of VSS of standard make, Fixing of Engraved AL plates for Alarm panel of various VCB Laying of 2.5Sqmm copper flexible wire for internal wiring . Fixing of digital frequency meter Fixing of Copper lugs and ferrules for internal wiring. Fixing of 4" Gang bells 24V DC Fixing of flow diagram with rading strip Fixing of HRC fuse units | Electrical work | Supply of DC Anunc.relay panel 8 feeders | As per relevaent standard specifications | 42500 | EA | 42500
2 | Erection of control/Relay panels,ACPanels,announciation panel set cin the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | electrical work | Erect-Contrl/Relay, AC, Announ. Panels | As per relevaent standard specifications | 1930 | EA | 3860
8 | Erection of 8.0 Mts PSCC Poles complete with necessary hard ware for yard lighting excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevaent standard specifications | 1500 | EA | 12000
8 | Fixing of Metal halide/LED lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5M GI pipe complete. | Electrical work | Fixing of LED/Metal halide complete. | As per relevaent standard specifications | 1268 | EA | 10144
8 | Supply and Fixing of junction box and Providing with proper Fuse protection and required glauds suitable for Cable Terminations. The box shall be fixed on the pole. | Electrical work | 33/11kv S.S Yard lighting junction box | As per relevaent standard specifications | 351.9 | EA | 2815.2
1 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply & fixing of marshall box | As per relevaent standard specifications | 3085.5 | EA | 3085.5
1 | Supply and fixing of filled sand bucket set complete (4 Nos. Buckets) with stand to mount fire buckets. | Electrical work | Sup Fire Buckets Stand with Buckets | As per relevaent standard specifications | 1386 | SET | 1386
2 | Supply and fixing of CO2 Cylinder set as per IS2878 Specifications. | Electrical work | Sup TrollyMounted Co2 Cylinders(IS-2878) | As per relevaent standard specifications | 9240 | EA | 18480
1 | Supplying and fixing of feeder indicator board to each of the 3Nos feeder breakers and LV breaker, danger boards made of 1'x1' and properly mounted on the structures. The letters written on the borad shall be 1.5"size with blue colour and background shall be of white colour | Electrical work | S&F-33/11KV SS Feeder Indicator Board | As per relevaent standard specifications | 551 | SET | 551
1 | Supply and fixing of wooden board of size 3'x2'.5'indicating the layout of the Switch yard. | Electrical work | Sup &fix of board ind Switchyard layout | As per relevaent standard specifications | 1654 | EA | 1654
1 | Supply and Erection of Permanent Name Board of on 3'x4' steel sheetmounted on steel frame as described in Specification. | Electrical work | Sup 33/11kv S.S Permanent name board | As per relevaent standard specifications | 10238 | EA | 10238
1 | Supply of Digital clamp meter. | Electrical work | Supply of Digital clamp meter. | As per relevaent standard specifications | 2888 | EA | 2888
1 | Supply of Rechargeable LED torch light of Standard make. | Electrical work | Sup Rechargeable LED torch light. | As per relevaent standard specifications | 1733 | EA | 1733
1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box containing ‘D’Spanners from size 6 to 54, Hammer small and big size, Ring spanners from 6 to 28, Adjustable spanner, Pipe wrench, Cutting Plier, Nose plier, Tester, insulated Screw drive. | Electrical work | SupTaparia Tool kit complete as per Spec | As per relevaent standard specifications | 4925 | SET | 4925
1 | Supply and fixing of safety instructions/Substation operation instruction board | Electrical work | Sup& fix safety inst/SS Op. inst board | As per relevaent standard specifications | 2205 | EA | 2205
8 | Supply of 25 W LED lamp with fitting of philips make | Electrical work | S-25W LED fixture set | As per relevaent standard specifications | 3200 | EA | 25600
1 | Supply of Alluminum Ladder(20 feet) | Electrical work | S-10ft Aluminium Ladder | As per relevaent standard specifications | 1654 | EA | 1654
1 | Supply of Megger (2000 ohms, 0-2.5kv) | Electrical work | Supply of Earth megger (1000v) | As per relevaent standard specifications | 8085 | EA | 8085
4 | Supply of Earth Discharging Rod 10' length. | Electrical work | S-Earth Rod 8ft Long 3mm Thick | As per relevaent standard specifications | 1000 | EA | 4000
450 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevaent standard specifications | 117.5 | KG | 52875
66 | Supply of PG clamps for panther 2 bolted 800 A. | Electrical work | S-Al. alloy three bolted PG clamps 800A | As per relevaent standard specifications | 130 | EA | 8580
350 | Supply and Laying of 2 core/4 core cable includes excavation earth and back filling with sand and earth in alternate layers as shown in the sketch. The cable termination shall be made by providing proper size of lugs at both ends of the cable termination. | Electrical work | 33/11kv S.S laying of 2/4core for light | As per relevaent standard specifications | 50 | M | 17500
31 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevaent standard specifications | 407.29 | EA | 12625.99
8 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevaent standard specifications | 271.52 | EA | 2172.16
2 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip. | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevaent standard specifications | 2720.34 | EA | 5440.68
10.5 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevaent standard specifications | 617.1 | TO | 6479.55
10.5 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevaent standard specifications | 221 | TO | 2320.5
10.5 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevaent standard specifications | 185 | TO | 1942.5
350 | Loading and unwinding of Panther conductor. | Electrical work | Load-Unwinding Panther conductor | As per relevaent standard specifications | 3 | M | 1050
350 | Unloading of Panther conductor. | Electrical work | Unload-Unwinding Panther conductor | As per relevaent standard specifications | 2 | M | 700
2 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevaent standard specifications | 2 | KI | 4
2 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevaent standard specifications | 2 | KI | 4
2 | Loading of 33KV Metal parts bag of 25 nos. | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevaent standard specifications | 65 | BAG | 130
2 | Unloading of 33 KV Metal parts bag of 25 nos. | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevaent standard specifications | 65 | BAG | 130
2 | Loading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | LOADING of 11kv Pin/Post/Solid Core Insu | As per relevaent standard specifications | 1 | KI | 2
2 | Unloading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | UNLOADING of 11kv Pin/Post/Solid Core In | As per relevaent standard specifications | 1 | KI | 2
600 | Loading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | Load-PVC Control Cable 10C | As per relevaent standard specifications | 1 | M | 600
600 | Unloading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | UnLoad-PVC Control Cable 10C | As per relevaent standard specifications | 1.02 | M | 612
1 | Loading of 3Ph 25KVA Distribution Transformer. | Electrical work | Load-3Ph 25KVA DTR | As per relevaent standard specifications | 252 | EA | 252
1 | UnLoading of 3Ph 25KVA Distribution Transformer. | Electrical work | UnLoad-3Ph 25KVA DTR | As per relevaent standard specifications | 202 | EA | 202
1 | Loading of 33/11 KV Current Transformers/ Potential Transformers. | Electrical work | LOADING of 33/11 KV CTs/ PTs | As per relevaent standard specifications | 165 | EA | 165
6 | Loading of 33 KV10 KA LAs Station type. | Electrical work | LOADING of 33 KV10 KA LAs Station type | As per relevaent standard specifications | 41 | EA | 246
6 | Unloading of 33 KV10 KA LAs Station type. | Electrical work | UNLOADING of 33 KV10 KA LAs Station type | As per relevaent standard specifications | 35 | EA | 210
9 | Loading of 11 KV10 KA LAs Line type. | Electrical work | LOADING of 11 KV, 10 KA LAs Line type | As per relevaent standard specifications | 32 | EA | 288
9 | Unloading of 11 KV10 KA LAs Line type. | Electrical work | UNLOADING of 11 KV, 10 KA LAs Line type | As per relevaent standard specifications | 32 | EA | 288
3 | Loading of 11 KV10 KA LAs Station type. | Electrical work | LOADING of 11 KV,10 KA LAs Station type | As per relevaent standard specifications | 32 | EA | 96
3 | Unloading of 11 KV10 KA LAs Station type. | Electrical work | UNLOADING of 11 KV,10 KA LAs Station typ | As per relevaent standard specifications | 32 | EA | 96
2 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevaent standard specifications | 126 | EA | 252
2 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevaent standard specifications | 79 | EA | 158
10 | loading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevaent standard specifications | 80 | EA | 800
10 | Unloading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevaent standard specifications | 80 | EA | 800
4 | Loading and Unloading of 12V/24V Battery Set. | Electrical work | Load/Unload-12V/24V Battery Set | As per relevaent standard specifications | 23 | EA | 92
2.66 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.76x0.76x0.152M with CC mix of ratio 1:3:6 Using form boxes (0.087 Cu.Mt)*31 with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevaent standard specifications | 6579 | M3 | 17500.14
1 | Erection of 11kv Potential Transformer sets complete including jumpering. The LV side of the PT shall be provided with proper fuse protection mounted in separate marshalling boxwith proper size cable glands etc. The box shall be mounted on the Substation structure. | Electrical work | Erection of 11kv three phase PT s | As per relevaent standard specifications | 800 | SET | 800
1 | Unloading of 33/11 KV Current Transformers/ Potential Transformers | Electrical work | UNLOADING of 33/11 KV CTs/ PTs | As per relevaent standard specifications | 128 | EA | 128
1 | Fixing of Distribution Box and Providing with proper Fuse protection system and reqired Cable Terminations at Station T/F LT side and AC/DC Panel and fixing meter. Power cable of adequate size shall be provided from station DTR to control room AC Panel. | Electrical work | Erection of LT distribution box | As per relevaent standard specifications | 1594.67 | EA | 1594.67
4.32 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.6x0.6x1.5M with CC mix of ratio 1:3:6 Using form boxes (0.546 Cu.Mt)*8 with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevaent standard specifications | 6579 | M3 | 28421.28
2 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply and fixing of PT Marshalling box | As per relevaent standard specifications | 1139.85 | EA | 2279.7
19 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the hard pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated hard rock bits if any and leveling the site without any lead. | Earth work | EXCAV. OF PIT HARD (2.6" x 2.6" x 5.0') | As per relevaent standard specifications | 1440 | EA | 27360
5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for First coat of 1st GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 1st coat Al. Painting. | As per relevaent standard specifications | 2181 | TO | 11995.5
5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 1st coat of Aluminium | Electrical work | Labour for 1st coat Al. Painting. | As per relevaent standard specifications | 851 | TO | 4680.5
5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for second coat of 2nd GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 2nd coat Al. Painting. | As per relevaent standard specifications | 1293 | TO | 7111.5
5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 2nd coat of Aluminium | Electrical work | Labour for 2nd coat Al. Painting. | As per relevaent standard specifications | 482 | TO | 2651
4.66 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 33 kv line | Earth work | survey line&cabl inc peg mark&tree clear | As per relevaent standard specifications | 765 | KM | 3564.9
74 | Excavation of Pole pits of size 0.76x0.76x1.52 for 11 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevaent standard specifications | 600 | EA | 44400
20 | Excavation of Pole pits of size 0.76x0.76x1.52 for 11 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the hard pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated hard rock bits if any and leveling the site without any lead. | Earth work | EXCAV. OF PIT HARD (2.6" x 2.6" x 5.0') | As per relevaent standard specifications | 1440 | EA | 28800
94 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevaent standard specifications | 4165.28 | EA | 391536.32
44 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevaent standard specifications | 2400 | EA | 105600
22 | Formation of 33 kv cut points (Vertical/Horizantal) including fixing of Clamps and top cleat and fixing of pin insulator complete with necessary hard wear for stud locations excluding the cost of pit Excavation and the pole shall be numbered with colour paint and earthing. | Electrical work | Horizontal Cut point for 33 KV line | As per relevaent standard specifications | 1759.5 | EA | 38709
65.176 | Concreting the location after erection of 11/9.1 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.75X0.75X2 Mts)* 48 = 54Cu.Mt and (0.45X0.45X1.265 Mts)* 44 = 11.176 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevaent standard specifications | 6579 | M3 | 428792.904
4.66 | Paving of the 100 sqmm AAA conductor and stringing duly arranging temporary guys, tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pin binding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Earth work | Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevaent standard specifications | 12600.06 | KM | 58716.2796
188 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevaent standard specifications | 117.5 | KG | 22090
94 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevaent standard specifications | 431.97 | EA | 40605.18
44 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevaent standard specifications | 407.29 | EA | 17920.76
4 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevaent standard specifications | 202 | EA | 808
4 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevaent standard specifications | 100 | EA | 400
4 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip. | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevaent standard specifications | 2720.34 | EA | 10881.36
1.05 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevaent standard specifications | 617.1 | TO | 647.955
1.05 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevaent standard specifications | 221 | TO | 232.05
1.05 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevaent standard specifications | 185 | TO | 194.25
47 | Loading of 33 KV Pin insulators | Electrical work | LOADING of 33 KV Pin insulators | As per relevaent standard specifications | 3 | KI | 141
47 | Unloading of 33 KV Pin insulators | Electrical work | UNLOADING of 33 KV Pin insulators | As per relevaent standard specifications | 3 | KI | 141
22 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevaent standard specifications | 2 | KI | 44
22 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevaent standard specifications | 2 | KI | 44
7 | Loading of 33KV Metal parts bag of 25 nos. | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevaent standard specifications | 65 | BAG | 455
7 | Unloading of 33 KV Metal parts bag of 25 nos. | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevaent standard specifications | 65 | BAG | 455
22 | Erection of 33 kv Stay set complete including fixing of bow ,fixing and binding of Eye bolt, Anchor rod, guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. | Electrical work | Assembly and erection of Stay set 33kv | As per relevaent standard specifications | 684.53 | SET | 15059.66
66 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In all soils except Hard gravel Hard Murram, Disintegrated Rock,Hard rock Requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevaent standard specifications | 520 | EA | 34320
115 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 75 x 8 mm MS Flat | Earth work | Fab Back clamps with 75 x 8 mm MS Flat | As per relevaent standard specifications | 31 | EA | 3565
88 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 75 x 8 mm MS Flat | Electrical work | Fab Stay clamps with 75x8 mm MM Flat | As per relevaent standard specifications | 42 | EA | 3696
138 | Numbering of poles incl. cost of paint | Electrical work | Numbering of poles incl. cost of paint | As per relevaent standard specifications | 32 | EA | 4416
5.63 | Concreting the stay location after erection of 11 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / stay set .Using form boxes (0.45X0.45X1.265 Mts)* 22 = 5.63 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevaent standard specifications | 6579 | M3 | 37039.77
5.22 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 11 kv line | Earth work | survey line&cabl inc peg mark&tree clear | As per relevaent standard specifications | 765 | KM | 3993.3
73 | Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevaent standard specifications | 600 | EA | 43800
30 | Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the hard pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated hard rock bits if any and leveling the site without any lead. | Earth work | EXCAV. OF PIT HARD (2.6" x 2.6" x 5.0') | As per relevaent standard specifications | 1440 | EA | 43200
38 | Erection of 8.0 Mts PSCC Poles complete with necessary hard ware for yard lighting excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevaent standard specifications | 1500 | EA | 57000
103 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevaent standard specifications | 2400 | EA | 247200
22 | Formation of 11 kv cut points (Vertical/Horizantal) including fixing of 11 KV Cross arms,clamps, strain insulators sets complete with hardware and stays (Bows and Eye-bolts), Excluding the cost of pit Excavation and pole erection. The contractor has to supply GI Bolts and Nuts. | Electrical work | Formatn of Horiz Cut point for 11KV line | As per relevaent standard specifications | 1350 | EA | 29700
42.973 | Concreting the location after erection of 9.1 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.76X0.76X1.52 Mts)* 38 = 33.32 Cu.Mt and (0.45X0.45X1.265 Mts)* 38 = 9.728 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevaent standard specifications | 6579 | M3 | 282719.367
5.22 | Paving of the conductor 55 Sqmm Single Circuit (3 Conductors) AAAC and stringing duly arranging temporary guys,tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pinbinding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing of 55sqmm 33/11kv Line 3 Cond | As per relevaent standard specifications | 8500 | KM | 44370
200 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevaent standard specifications | 117.5 | KG | 23500
1.04 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevaent standard specifications | 221 | TO | 229.84
1.04 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevaent standard specifications | 185 | TO | 192.4
309 | Loading 11KV Polymer Pin Insulator with GI pins | Electrical work | Load-11KV Polymer Pin Insulator-GI pin | As per relevaent standard specifications | 1 | EA | 309
309 | Unloading 11KV Polymer Pin Insulator with GI pins | Electrical work | Unload-11KV Polymer Pin Insulator-GI pin | As per relevaent standard specifications | 1 | EA | 309
1.04 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevaent standard specifications | 587.52 | TO | 611.0208
3 | Transport of VCB , Control pannels, current transformater, bosster etc, above 20 KM and upto 30 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs >20 & <30Km | As per relevaent standard specifications | 3691.38 | EA | 11074.14
3 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevaent standard specifications | 202 | EA | 606
3 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevaent standard specifications | 100 | EA | 300
38 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevaent standard specifications | 271.52 | EA | 10317.76
103 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevaent standard specifications | 407.29 | EA | 41950.87
84 | Loading of 11 KV V - Cross arms | Electrical work | LOADING of 11 KV V - Cross arms | As per relevaent standard specifications | 4 | EA | 336
84 | Unloading of 11 KV V - Cross arms | Electrical work | UNLOADING of 11 KV V - Cross arms | As per relevaent standard specifications | 4 | EA | 336
7 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevaent standard specifications | 48 | BAG | 336
7 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevaent standard specifications | 48 | BAG | 336
84 | Loading of 11 KV Top fittings | Electrical work | LOADING of 11 KV Top fittings | As per relevaent standard specifications | 1 | EA | 84
84 | Unloading of 11 KV Top fittings | Electrical work | UNLOADING of 11 KV Top fittings | As per relevaent standard specifications | 1 | EA | 84
9 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevaent standard specifications | 2 | KI | 18
9 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevaent standard specifications | 2 | KI | 18
19 | Erection of 11 kv Stay set complete including fixing of bow, fixing and binding of Eye bolt,Anchor rod,guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. The contractor has to supply GI Bolts and Nuts. | Earth work | Assembly and erection of Stay set11kv&LT | As per relevaent standard specifications | 606.85 | SET | 11530.15
57 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In all soils except Hard gravel Hard Murram, Disintegrated Rock,Hard rock Requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevaent standard specifications | 520 | EA | 29640
42 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 50 x 6 mm MS Flat | Electrical work | Fab Back clamps with 50 x 6 mm MS Flat | As per relevaent standard specifications | 15 | EA | 630
32 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 50 x 6 mm MS Flat | Electrical work | Fab Stay clamps with 50 x 6 mm MS Flat | As per relevaent standard specifications | 25 | EA | 800
141 | Numbering of poles incl. cost of paint | Electrical work | Numbering of poles incl. cost of paint | As per relevaent standard specifications | 32 | EA | 4512
4.8 | Concreting the stay location after erection of 9.1 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / stay set .Using form boxes (0.45X0.45X1.265 Mts)* 19 = 4.8 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevaent standard specifications | 6579 | M3 | 31579.2
2 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevaent standard specifications | 4500 | EA | 9000
4 | Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevaent standard specifications | 600 | EA | 2400
8 | Erection of 8.0 Mts PSCC Poles complete with necessary hard ware for yard lighting excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevaent standard specifications | 1500 | EA | 12000
4 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevaent standard specifications | 2400 | EA | 9600
5.55 | Concreting the location after erection of 9.1/8 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.76X0.76X1.52 Mts)* 4 = 3.508Cu.Mt and (0.45X0.45X1.265 Mts)* 8 = 2.048 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevaent standard specifications | 6579 | M3 | 36513.45
5 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevaent standard specifications | 117.5 | KG | 587.5
0.67 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevaent standard specifications | 221 | TO | 148.07
0.67 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevaent standard specifications | 185 | TO | 123.95
0.67 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevaent standard specifications | 587.52 | TO | 393.6384
8 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevaent standard specifications | 271.52 | EA | 2172.16
4 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevaent standard specifications | 407.29 | EA | 1629.16
1 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevaent standard specifications | 48 | BAG | 48
1 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevaent standard specifications | 48 | BAG | 48
1 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevaent standard specifications | 2 | KI | 2
1 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevaent standard specifications | 2 | KI | 2
4 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevaent standard specifications | 3486 | EA | 13944
4 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevaent standard specifications | 1234.2 | EA | 4936.8
60 | Supply of earthing GI Flat 25X3 mm including material | Earth work | S-Earthing GI flat 25x3 mm incl material | As per relevaent standard specifications | 105 | KG | 6300
2 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevaent standard specifications | 126 | EA | 252
2 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevaent standard specifications | 79 | EA | 158
8 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In all soils except Hard gravel Hard Murram, Disintegrated Rock,Hard rock Requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevaent standard specifications | 520 | EA | 4160
3 | Erection of 11kV AB Switches 800/400 Amps includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevaent standard specifications | 3200 | EA | 9600
10 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevaent standard specifications | 117.5 | KG | 1175
0.26 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevaent standard specifications | 221 | TO | 57.46
0.26 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevaent standard specifications | 185 | TO | 48.1
0.26 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevaent standard specifications | 587.54 | TO | 152.7604
3 | Supply of C I earth pipe of size 50mm dia, 2 mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 50mm dia 2m long | As per relevaent standard specifications | 2441 | EA | 7323
6 | Loading/Unloading of C I earth pipe of size 80/50mm dia, 2 mtrs long for earth electrode | Electrical work | Load/Unload-CI pipe 80/50 mm dia 2mt L | As per relevaent standard specifications | 18 | EA | 108
3 | Providing of collar rings of 450mm dia at 4 pole structure | Electrical work | Collar/ Rings of 450mm dia | As per relevaent standard specifications | 250 | EA | 750
30 | Supply of earthing GI Flat 25X3 mm including material | Earth work | S-Earthing GI flat 25x3 mm incl material | As per relevaent standard specifications | 105 | KG | 3150
3 | loading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevaent standard specifications | 80 | EA | 240
3 | Unloading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevaent standard specifications | 80 | EA | 240
2.46 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 33 kv line | Earth work | survey line&cabl inc peg mark&tree clear | As per relevaent standard specifications | 765 | KM | 1881.9
35 | Excavation of Pole pits of size 0.75x0.75x2 for 11 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevaent standard specifications | 600 | EA | 21000
15 | Excavation of Pole pits of size 0.75x0.75x2 for 11 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the hard pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated hard rock bits if any and leveling the site without any lead. | Earth work | EXCAV. OF PIT HARD (2.6" x 2.6" x 5.0') | As per relevaent standard specifications | 1440 | EA | 21600
50 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevaent standard specifications | 4165.28 | EA | 208264
30 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevaent standard specifications | 2400 | EA | 72000
16 | Formation of 33 kv cut points (Vertical/Horizantal) including fixing of Clamps and top cleat and fixing of pin insulator complete with necessary hard wear for stud locations excluding the cost of pit Excavation and the pole shall be numbered with colour paint and earthing. | Electrical work | Horizontal Cut point for 33 KV line | As per relevaent standard specifications | 1759.5 | EA | 28152
38.05 | Concreting the location after erection of 11/9.1 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.75X0.75X2 Mts)* 27 = 30.37Cu.Mt and (0.45X0.45X1.265 Mts)* 30 = 7.68 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevaent standard specifications | 6579 | M3 | 250330.95
2.46 | Paving of the 100 sqmm AAA conductor and stringing duly arranging temporary guys, tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pin binding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Earth work | Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevaent standard specifications | 12600.06 | KM | 30996.1476
100 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevaent standard specifications | 117.5 | KG | 11750
50 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevaent standard specifications | 431.97 | EA | 21598.5
30 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevaent standard specifications | 407.29 | EA | 12218.7
2 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevaent standard specifications | 202 | EA | 404
2 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevaent standard specifications | 100 | EA | 200
2 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip. | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevaent standard specifications | 2720.34 | EA | 5440.68
0.775 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevaent standard specifications | 617.1 | TO | 478.2525
0.775 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevaent standard specifications | 221.01 | TO | 171.2827
0.775 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevaent standard specifications | 185.01 | TO | 143.3827
26 | Loading of 33 KV Pin insulators | Electrical work | LOADING of 33 KV Pin insulators | As per relevaent standard specifications | 3 | KI | 78
26 | Unloading of 33 KV Pin insulators | Electrical work | UNLOADING of 33 KV Pin insulators | As per relevaent standard specifications | 3 | KI | 78
17 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevaent standard specifications | 2 | KI | 34
17 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevaent standard specifications | 2 | KI | 34
4 | Loading of 33KV Metal parts bag of 25 nos. | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevaent standard specifications | 65 | BAG | 260
4 | Unloading of 33 KV Metal parts bag of 25 nos. | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevaent standard specifications | 65 | BAG | 260
10 | Erection of 33 kv Stay set complete including fixing of bow ,fixing and binding of Eye bolt, Anchor rod, guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. | Electrical work | Assembly and erection of Stay set 33kv | As per relevaent standard specifications | 684.53 | SET | 6845.3
40 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In all soils except Hard gravel Hard Murram, Disintegrated Rock,Hard rock Requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevaent standard specifications | 520 | EA | 20800
90 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 75 x 8 mm MS Flat | Electrical work | Fab Stay clamps with 75x8 mm MM Flat | As per relevaent standard specifications | 42 | EA | 3780
80 | Numbering of poles incl. cost of paint | Electrical work | Numbering of poles incl. cost of paint | As per relevaent standard specifications | 32 | EA | 2560
2.56 | Concreting the stay location after erection of 11 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / stay set .Using form boxes (0.45X0.45X1.265 Mts)* 10 = 2.56 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevaent standard specifications | 6579 | M3 | 16842.24
3 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevaent standard specifications | 4500 | EA | 13500
4 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevaent standard specifications | 700 | EA | 2800
4 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevaent standard specifications | 4165.28 | EA | 16661.12
8 | Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevaent standard specifications | 600 | EA | 4800
8 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevaent standard specifications | 2400 | EA | 19200
6.54 | Concreting the location after erection of 11/9.1 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.75X0.75X2 Mts)* 4 = 4.5Cu.Mt and (0.45X0.45X1.265 Mts)* 8 = 2.048 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevaent standard specifications | 6579 | M3 | 43026.66
20 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevaent standard specifications | 117.5 | KG | 2350
1 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevaent standard specifications | 221 | TO | 221
1 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevaent standard specifications | 185 | TO | 185
1 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevaent standard specifications | 587.52 | TO | 587.52
8 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevaent standard specifications | 407.29 | EA | 3258.32
4 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevaent standard specifications | 431.97 | EA | 1727.88
1 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevaent standard specifications | 48 | BAG | 48
1 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevaent standard specifications | 48 | BAG | 48
2 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevaent standard specifications | 2 | KI | 4
2 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevaent standard specifications | 2 | KI | 4
6 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevaent standard specifications | 3486 | EA | 20916
6 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevaent standard specifications | 1234.2 | EA | 7405.2
50 | Supply of earthing GI Flat 25X3 mm including material | Earth work | S-Earthing GI flat 25x3 mm incl material | As per relevaent standard specifications | 105 | KG | 5250
3 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevaent standard specifications | 126 | EA | 378
3 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevaent standard specifications | 79 | EA | 237
12 | Hire-JCB to Level & Clear the Site | Civil work | Hire-JCB to Level & Clear the Site | As per relevaent standard specifications | 2165.7 | H | 25988.4
96.7 | Excavation in Ordinary Soil | Civil work | Excavation in Ordinary Soil | As per relevaent standard specifications | 366 | M3 | 35392.2
18.2 | PCC with 40mm Metal (1:4:8) | Civil work | PCC with 40mm Metal (1:4:8) | As per relevaent standard specifications | 4058 | M3 | 73855.6
116.3 | CRS Masonary CM(1:6) 2nd Sort | Civil work | CRS Masonary CM(1:6) 2nd Sort | As per relevaent standard specifications | 4083 | M3 | 474852.9
23.1 | Brick Masonary in CM(1:6) GFloor | Civil work | Brick Masonary in CM(1:6) GFloor | As per relevaent standard specifications | 8103 | M3 | 187179.3
695 | S&Filling with Borrowed Gravel | Civil work | S&Filling with Borrowed Gravel | As per relevaent standard specifications | 485 | M3 | 337075
5.9 | RCC Footing: M20Gr, Steel Centering | Civil work | RCC Footing: M20Gr, Steel Centering | As per relevaent standard specifications | 8306 | M3 | 49005.4
2.8 | RCC Column GF: M20Gr, Steel Centering | Civil work | RCC Column GF: M20Gr, Steel Centering | As per relevaent standard specifications | 11181 | M3 | 31306.8
2.6 | RCC Plinth Beam: M20Gr, Steel Centering | Civil work | RCC Plinth Beam: M20Gr, Steel Centering | As per relevaent standard specifications | 10923 | M3 | 28399.8
0.7 | RCC Lintel GF: M20Gr, Steel Centering | Civil work | RCC Lintel GF: M20Gr, Steel Centering | As per relevaent standard specifications | 11372 | M3 | 7960.4
13.5 | RCC Sunshade GF: M20Gr, Steel Centering | Civil work | RCC Sunshade GF: M20Gr, Steel Centering | As per relevaent standard specifications | 1210 | M2 | 16335
2.9 | RCC Roof Beam GF: M20Gr, Steel Centering | Civil work | RCC Roof Beam GF: M20Gr, Steel Centering | As per relevaent standard specifications | 10982 | M3 | 31847.8
10.2 | RCC Roof Slab GF: M20Gr, Steel Centering | Civil work | RCC Roof Slab GF: M20Gr, Steel Centering | As per relevaent standard specifications | 10496 | M3 | 107059.2
2.5 | Reinforcement Steel Fe 415/500 | Civil work | Reinforcement Steel Fe 415/500 | As per relevaent standard specifications | 72726 | TON | 181815
404.66 | Plastering 20mm (16mm+4mm)GFloor | Civil work | Plastering 20mm (16mm+4mm)GFloor | As per relevaent standard specifications | 422 | M2 | 170766.52
124.2 | Raised Pointing to CRS Masonary CM(1:3) | Civil work | Raised Pointing to CRS Masonary CM(1:3) | As per relevaent standard specifications | 95 | M2 | 11799
78.1 | Impervious Coat 20mm CM(1:3) GFloor | Civil work | Impervious Coat 20mm CM(1:3) GFloor | As per relevaent standard specifications | 450 | M2 | 35145
5.7 | S&F MT Wood Frame & Door-Laminate | Civil work | S&F MT Wood Frame & Door-Laminate | As per relevaent standard specifications | 6871 | M2 | 39164.7
5.76 | S&F Powder Coated Al Window | Civil work | S&F Powder Coated Al Window | As per relevaent standard specifications | 3572 | M2 | 20574.72
6.25 | S&F of MS Safety Grill | Civil work | S&F of MS Safety Grill | As per relevaent standard specifications | 2622 | M2 | 16387.5
39.2 | Polished Shabad Flooring 20mm CM(1:3) | Civil work | Polished Shabad Flooring 20mm CM(1:3) | As per relevaent standard specifications | 534 | M2 | 20932.8
10.7 | Polished Shabad Skirting CM(1:3) | Civil work | Polished Shabad Skirting CM(1:3) | As per relevaent standard specifications | 603 | M2 | 6452.1
25.2 | PCC with 40mm Metal (1:3:6) | Civil work | PCC with 40mm Metal (1:3:6) | As per relevaent standard specifications | 4336 | M3 | 109267.2
5.1 | PCC with 20mm Metal (1:2:4) | Civil work | PCC with 20mm Metal (1:2:4) | As per relevaent standard specifications | 5469 | M3 | 27891.9
49.5 | S&Spreading of 20mm HBG Metal | Civil work | S&Spreading of 20mm HBG Metal | As per relevaent standard specifications | 1618 | M3 | 80091
110 | S&F MS Security Fencing Mesh (2"X2") | Civil work | S&F MS Security Fencing Mesh (2"X2") | As per relevaent standard specifications | 2108 | M2 | 231880
10.55 | S&F MS Gate | Civil work | S&F MS Gate | As per relevaent standard specifications | 4676.9 | M2 | 49341.295
121.2 | Painting with OBD 2Coats+Primer | Civil work | Painting with OBD 2Coats+Primer | As per relevaent standard specifications | 115 | M2 | 13938
178.4 | Painting SnowCem/Apex 2 Coats+Primer | Civil work | Painting SnowCem/Apex 2 Coats+Primer | As per relevaent standard specifications | 205 | M2 | 36572
175.9 | Painting with SuryaCem of 3 Coat | Civil work | Painting with SuryaCem of 3 Coat | As per relevaent standard specifications | 73 | M2 | 12840.7
30 | S&F Conceal PVC Pipe 25mm dia in Slab | Civil work | S&F Conceal PVC Pipe 25mm dia in Slab | As per relevaent standard specifications | 90 | M | 2700
20 | S&F Conceal PVC Pipe 25mm dia in Wall | Civil work | S&F Conceal PVC Pipe 25mm dia in Wall | As per relevaent standard specifications | 93 | M | 1860
15 | S&F Modular Switch LP,FP,EFP for NRBuild | Civil work | S&F Modular Switch LP,FP,EFP for NRBuild | As per relevaent standard specifications | 602 | EA | 9030
2 | S&F Modular 3/2pin 6A Sockets | Civil work | S&F Modular 3/2pin 6A Sockets | As per relevaent standard specifications | 493 | EA | 986
2 | S&F Modular 3pin 16/6A Sockets | Civil work | S&F Modular 3pin 16/6A Sockets | As per relevaent standard specifications | 455 | EA | 910
4 | S&F Batten Holder | Civil work | S&F Batten Holder | As per relevaent standard specifications | 224 | EA | 896
4 | S&F 20W LED Retro Tube Light | Civil work | S&F 20W LED Retro Tube Light | As per relevaent standard specifications | 876.5 | EA | 3506
90 | S&R 2 of 14/0.3mm (1.0sqmm) (FR) | Civil work | S&R 2 of 14/0.3mm (1.0sqmm) (FR) | As per relevaent standard specifications | 49 | M | 4410
30 | S&R 2 of 36/0.3mm (2.5sqmm) (FR) | Civil work | S&R 2 of 36/0.3mm (2.5sqmm) (FR) | As per relevaent standard specifications | 100 | M | 3000
1 | S&F 8wySPNDB IP-20,10kA-6-32A SPMCB 4No | Civil work | S&F 8wySPNDB IP-20,10kA-6-32A SPMCB 4No | As per relevaent standard specifications | 5368 | EA | 5368
1 | Provd-Independent Earthing | Civil work | Provd-Independent Earthing | As per relevaent standard specifications | 5169 | EA | 5169
15 | S&R No.8 SWG Copper Wire | Civil work | S&R No.8 SWG Copper Wire | As per relevaent standard specifications | 153 | M | 2295
2 | S&F 1200mm (48'') Sweep Ceiling Fan | Civil work | S&F 1200mm (48'') Sweep Ceiling Fan | As per relevaent standard specifications | 2225 | EA | 4450
13.7 | Ceramic Tile Flooring 20mm CM(1:3) | Civil work | Ceramic Tile Flooring 20mm CM(1:3) | As per relevaent standard specifications | 949 | M2 | 13001.3
1 | S&F Orissa Pan WC 580mmx440mm | Civil work | S&F Orissa Pan WC 580mmx440mm | As per relevaent standard specifications | 2207 | EA | 2207
2 | S&F Floor Trap (Bell Mouth) 110mm | Civil work | S&F Floor Trap (Bell Mouth) 110mm | As per relevaent standard specifications | 269 | EA | 538
2 | S&F 90mm dia Plain Bend PVC/SWR Pipe | Civil work | S&F 90mm dia Plain Bend PVC/SWR Pipe | As per relevaent standard specifications | 84 | EA | 168
1 | S&F 75mm dia Door Bend PVC/SWR Pipe | Civil work | S&F 75mm dia Door Bend PVC/SWR Pipe | As per relevaent standard specifications | 81 | EA | 81
1 | S&F 150mmx100mm SWG Gully Trap | Civil work | S&F 150mmx100mm SWG Gully Trap | As per relevaent standard specifications | 749 | EA | 749
6 | S&F 110mm dia 3M 1Socket PVC/SWR Pipe | Civil work | S&F 110mm dia 3M 1Socket PVC/SWR Pipe | As per relevaent standard specifications | 428 | M | 2568
1 | S&F 4" dia PVC Cowl | Civil work | S&F 4" dia PVC Cowl | As per relevaent standard specifications | 23 | EA | 23
1 | Construct- 4' dia & 5' Ht Soak Pit | Civil work | Construct- 4' dia & 5' Ht Soak Pit | As per relevaent standard specifications | 4904 | EA | 4904
100 | S&F 22.20mm OD CPVC Pipe-SDR 11 | Civil work | S&F 22.20mm OD CPVC Pipe-SDR 11 | As per relevaent standard specifications | 417 | M | 41700
100 | S&F 28.60mm OD CPVC Pipe-SDR 11 | Civil work | S&F 28.60mm OD CPVC Pipe-SDR 11 | As per relevaent standard specifications | 514 | M | 51400
24 | S&F-15mm GM/Bronze Ball Valve | Civil work | S&F-15mm GM/Bronze Ball Valve | As per relevaent standard specifications | 230 | EA | 5520
1 | S&F-20mm GM/Bronze Ball Valve | Civil work | S&F-20mm GM/Bronze Ball Valve | As per relevaent standard specifications | 331 | EA | 331
2 | S&F-25mm GM/Bronze Ball Valve | Civil work | S&F-25mm GM/Bronze Ball Valve | As per relevaent standard specifications | 466 | EA | 932
4 | S&F-15mm Bib Tap 400gm Full turn | Civil work | S&F-15mm Bib Tap 400gm Full turn | As per relevaent standard specifications | 275 | EA | 1100
500 | S&F Polyethylene Water Storage Tank | Civil work | S&F Polyethylene Water Storage Tank | As per relevaent standard specifications | 10 | L | 5000
1 | Supply of Table 4'x2' with MS Frame | Civil work | Supply of Table 4'x2' with MS Frame | As per relevaent standard specifications | 4350 | EA | 4350
1 | Supply of S-Type Chair | Civil work | Supply of S-Type Chair | As per relevaent standard specifications | 4035 | EA | 4035
2 | Supply of PVC Chair | Civil work | Supply of PVC Chair | As per relevaent standard specifications | 1200 | EA | 2400
2.5 | S&F Glow Sign Board | Civil work | S&F Glow Sign Board | As per relevaent standard specifications | 3735 | M2 | 9337.5
1.35 | S&F MS Board | Civil work | S&F MS Board | As per relevaent standard specifications | 4545 | M2 | 6135.75
7.3 | S&F RCC Hume Pipe of 450mm dia | Civil work | S&F RCC Hume Pipe of 450mm dia | As per relevaent standard specifications | 1345 | M | 9818.5
165 | S&F RCC Fencing Pole 0.115mx0.115mx2.7m | Civil work | S&F RCC Fencing Pole 0.115mx0.115mx2.7m | As per relevaent standard specifications | 1443 | EA | 238095
35 | S&F RCC Fencing Pole 0.1mx0.1mx1.8m | Civil work | S&F RCC Fencing Pole 0.1mx0.1mx1.8m | As per relevaent standard specifications | 1299 | EA | 45465
300 | S&F Barbed Wire 8H & 2Cross | Civil work | S&F Barbed Wire 8H & 2Cross | As per relevaent standard specifications | 260 | M | 78000
1 | Provd-Supply of Electricity to Site | Civil work | Provd-Supply of Electricity to Site | As per relevaent standard specifications | 5678 | EA | 5678
1 | Geophysical Investgation Charges | Civil work | Geophysical Investgation Charges | As per relevaent standard specifications | 7000 | EA | 7000
90 | Drilling-165mm Bore Well 0 to 90M | Civil work | Drilling-165mm Bore Well 0 to 90M | As per relevaent standard specifications | 336 | M | 30240
30 | Drill-165mm Bore Well 90M to 120M | Civil work | Drill-165mm Bore Well 90M to 120M | As per relevaent standard specifications | 389 | M | 11670
30 | Drill-165mm Bore Well 120M to 150M | Civil work | Drill-165mm Bore Well 120M to 150M | As per relevaent standard specifications | 407 | M | 12210
30 | S&F 160mm dia PVC Casing | Civil work | S&F 160mm dia PVC Casing | As per relevaent standard specifications | 1650 | M | 49500
1 | S&E SP SubMrsbl Pumpset 2.0HP 30 Stages | Civil work | S&E SP SubMrsbl Pumpset 2.0HP 30 Stages | As per relevaent standard specifications | 34894 | EA | 34894
200 | S&R 3C 2.5sqmm Flat Copper Cable | Civil work | S&R 3C 2.5sqmm Flat Copper Cable | As per relevaent standard specifications | 210 | M | 42000
1 | S&E D.O.L Starter 250V Single Phase | Civil work | S&E D.O.L Starter 250V Single Phase | As per relevaent standard specifications | 2400 | EA | 2400
1 | Supply & fixing of Flange Clamps | Civil work | Supply & ixing of Flange Clamps | As per relevaent standard specifications | 191 | EA | 191
178 | S&F-HDPE Pipe 40mm dia 16kg/sqcm-SDR 9 | Civil work | S&F-HDPE Pipe 40mm dia 16kg/sqcm-SDR 9 | As per relevaent standard specifications | 155 | M | 27590
92.5 | Seigniorage Charges - Sand | Civil work | Seigniorage Charges - Sand | As per relevaent standard specifications | 40 | M3 | 3700
80.1 | Seigniorage Charges - Metal | Civil work | Seigniorage Charges - Metal | As per relevaent standard specifications | 97.5 | M3 | 7809.75
695 | Seigniorage Charges - Gravel | Civil work | Seigniorage Charges - Gravel | As per relevaent standard specifications | 30 | M3 | 20850