## Sheet1
Estimate Quantity (only Figures) | Item Detailed Specification Description | Work Type eg. Earth Work, Electrical works.. etc ( upto 200 Characters) | Item Short Description ( upto 100 Characters) | APSS / Morth Cl. Number ( upto 200 Characters) | Rate (INR) ( Upto 2 Decimals ) | UOM ( upto 50 Characters) | Amount (INR) ( Upto 2 Decimals )
39 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 23400
31 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 74400
31.555 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.76x0.76x1.52M for 9.1mts poles and 0.6x0.6x 1.5 for 8 mts bpoles with CC mix of ratio 1:3:6 Using form boxes (0.88 Cu.Mt)*31 and (0.546 cu.mt)*8 with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 207600.345
0.961 | ERECTION OF S.S. STRUCTURE: Coping of 0.45x0.45x0.45Mt with 1:8 slope Using form boxes (0.031Cumt.) | Civil work | Coping & Muffing-Iron Pole | As per relevent standard specification | 3893 | M3 | 3741.173
31 | Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of poles with two coats of white cement (including cost of paint). | Electrical work | Paint-9.1M PSCC Poles as desc SSR | As per relevent standard specification | 485 | EA | 15035
5.5 | Fabrication of 100 X 50mm MS Channel for formation of 11kV and 33kV bays: Fabrication and erection of M.S,Channel 100x50mm for forming of 33KV & 11 KV Bays as per standard specifications to facilitate stringing of bus, erection of LA sets, AB Switches bolts & Nuts etc. including painting with one coats of red oxide and two coats of Aluminium paint. GI bolts&nuts shall be used. | Electrical work | Fabr & Erect-MS Chnl 100x50mm for SS Bay | As per relevent standard specification | 6600 | TO | 36300
118.5 | Erection of 33kV and 11kV Strung Bus with Panther (200Sqmm) ACSR Conductor: Erection of 33kV and 11kV Bus over the Substation structures with 200sqmm Panther ACSR conductor and giving Jumpers to connect the Switch gear by providing the suitable T clamps and round clamps suitable to Post type insulators & Insulators. | Electrical work | Stringing of bus with panther conductor | As per relevent standard specification | 327.68 | M | 38830.08
2 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 9000
9 | Erection of 11kV AB Switches 800/400 Amps includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 28800
3 | Supply & erection of 11 kV 400 A convential single(1/3) phasing AB switches.includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | S&E-400A 11KV ABSwth Conv 1ph(1/3) in SS | As per relevent standard specification | 4232 | EA | 12696
2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt). | Electrical work | Hoisting post ins&hrd wr 1panther 33kv | As per relevent standard specification | 781 | EA | 1562
4 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Electrical work | Hoisting post ins&hrd wr 1panther 11kv | As per relevent standard specification | 507 | EA | 2028
11 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 1562
16.46 | Excavation of pit in all types of soils of size 2.2x2.2x0.85Mts.for Construction of Plinths for VCB (33KV & 11 KV ) | Earth work | Excavate-Pit for 33KV VCB | As per relevent standard specification | 331 | M3 | 5448.26
22.264 | Providing of Base concreting (2.2x2.2x0.15 Mts) with 1:3:6 Concrete mix. Using form boxes, Providing of Concreting (2x2x1.0mts) with 1:3:6 Cocrete mix. Plastering of the plinth for smooth finishing with 12mm thick 1:3 cement motor and providing two coats white washing for part of the plinth above groung level. | Civil work | Cement concrete with 40MM metal VCB plin | As per relevent standard specification | 5160 | M3 | 114882.24
4 | Erection of Switchgear complete for 11 kV VCB includes Assembling the VCB Structures and mounting the VCBs over the already erected foudation including wiring of Breaker Control Panel/CTs, erection of CTs and control pannel providing Jumpers. | Electrical work | Erection of 11kv VCB | As per relevent standard specification | 12000 | EA | 48000
2 | Erection of 33KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 33kv LA stn type incl earthing | As per relevent standard specification | 880 | SET | 1760
1 | Erection of 11 KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 11kv LA stn type incl earthing | As per relevent standard specification | 559 | SET | 559
3 | Erection of 11 KV Lightening Arrestors line type complete including jumpering. | Electrical work | Erect of 11kvLA line type incl earthing | As per relevent standard specification | 505 | SET | 1515
1 | Supply of 33kv HG fuse set including providing of jumpers | Electrical work | S-33KV HG Fuse Set excl Ins & Chnl | As per relevent standard specification | 6431 | SET | 6431
1 | Erection of 33kv HG fuse set including providing of jumpers | Electrical work | Erect. of 33kv HG Fuseset incl earthing | As per relevent standard specification | 1331.81 | SET | 1331.81
1 | Supply of 11kv HG fuse set including providing of jumpers | Electrical work | S-11KV HG Fuse Set | As per relevent standard specification | 1733.75 | SET | 1733.75
1 | Erection of 11kv HG fuse set including providing of jumpers | Electrical work | Erect. of 11kv HG Fuseset incl earthing | As per relevent standard specification | 740.52 | SET | 740.52
23 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 80178
23 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 28386.6
500 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification.75x8 mm MS flat for Earth mat and connecting to electrodes. | Electrical work | Laying of earth mat,excavation 75x 8mm | As per relevent standard specification | 65 | RMT | 32500
950 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification. 50x6 mm MS flat for raisers, double flat shall be run for structure poles raisers & equipment earthing. | Electrical work | Earthing for raisers of SS Flat 50x6 mm. | As per relevent standard specification | 41 | RMT | 38950
2 | Providing of double earthing for neutral with flexible copper jumpers of adequate size including arrangement by fixing M.S.Channel 100x50mm. | Electrical work | SupCU Flexi jumper for Power T/F Neutral | As per relevent standard specification | 4725 | EA | 9450
4 | Erection of 24 Volts Battery along with Charger on the VCB plinth and giving DC supply to VCB's. | Electrical work | Erect-24V Batery with Chrgr incl grot-SS | As per relevent standard specification | 1050 | EA | 4200
700 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable includes excavation of earth and back filling with sand and earth in alternate layers . The cable termination shall be made by providing proper size lugs and shall be identified with colours. | Electrical work | Laying-4 core cable | As per relevent standard specification | 15 | RMT | 10500
1 | Erection of 25 KVA Three phase Station Transformer on the Substation Structures and giving jumpers/connections on HT side to the 11kV bus. Belting angle shall be provided both sides of DTR for securing DTR firmly in position. | Electrical work | Erection of Three Phase DTRs | As per relevent standard specification | 1139.95 | EA | 1139.95
1 | Supply of AC Panel Board includes: Fixing of 1 No.100A, MCCB, 10kA capacity of any standard make including material cost. Fixing of suitable panel box 3x3x1 with M.S.Sheet of 16 SWG with front door compartments inclusive of material cost & powder coating (with C Channel ). Fabrication of panel Fixing of 96x96mm analog voltmeter with VSS switch Fixing of 20A HRC fuse Fixing of 3 phase supply indicator kwith HRC fuses Supply and fixing of 6 Sqmm copper flexible wire (PVC) Fixing of Stud type TBs for outgoing feeder Fixing of Epoxy bus supports. | Electrical work | Supply of AC Supply panel complete | As per relevent standard specification | 42000 | EA | 42000
1 | Supply of DC Panel Board Fixing of suitable panel box of size 6'x6'x1' with M S sheet of 16 SWG with back doors (4'x6') and on front side with provision to fix up bakelite hylam sheet size of 4'x6' including cost of the panel with powder coating. Fixing of best quality of angles for panel. Fixing of C Channelfor panel. Fabrication of control panel including making suitable holes and board Fixing of Stud type TBs for outgoing feeder Fixing of 24V DC pilot lamps of standard make Fixing of healthy trip push buttons with LED lamp Fixing of plain switches for alarm acceptance and for PTR signal Fixing of ON/OFF push buttons Fixing of digital volt meter for 11kV Fixing of VSS of standard make, Fixing of Engraved AL plates for Alarm panel of various VCB Laying of 2.5Sqmm copper flexible wire for internal wiring . Fixing of digital frequency meter Fixing of Copper lugs and ferrules for internal wiring. Fixing of 4" Gang bells 24V DC Fixing of flow diagram with rading strip Fixing of HRC fuse units | Electrical work | Supply of DC Anunc.relay panel 8 feeders | As per relevent standard specification | 42500 | EA | 42500
1 | fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supplied by tenderer. | Electrical work | 33/11kv S.S Erection of AC&DC Panel | As per relevent standard specification | 7871.85 | SET | 7871.85
8 | Erection of 8.0 Mts PSCC Poles complete with necessary hard ware for yard lighting excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 12000
8 | Fixing of Metal halide/LED lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5M GI pipe complete. | Electrical work | Fixing of LED/Metal halide complete. | As per relevent standard specification | 1268 | EA | 10144
8 | Supply and Fixing of junction box and Providing with proper Fuse protection and required glauds suitable for Cable Terminations. The box shall be fixed on the pole. | Electrical work | 33/11kv S.S Yard lighting junction box | As per relevent standard specification | 351.9 | EA | 2815.2
2 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply & fixing of marshall box | As per relevent standard specification | 3085.5 | EA | 6171
1 | Supply and fixing of filled sand bucket set complete (4 Nos. Buckets) with stand to mount fire buckets. | Electrical work | Sup Fire Buckets Stand with Buckets | As per relevent standard specification | 1386 | SET | 1386
2 | Supply and fixing of CO2 Cylinder set as per IS2878 Specifications. | Electrical work | Sup TrollyMounted Co2 Cylinders(IS-2878) | As per relevent standard specification | 9240 | EA | 18480
1 | Supplying and fixing of feeder indicator board to each of the 3Nos feeder breakers and LV breaker, danger boards made of 1'x1' and properly mounted on the structures. The letters written on the borad shall be 1.5"size with blue colour and background shall be of white colour | Electrical work | S&F-33/11KV SS Feeder Indicator Board | As per relevent standard specification | 551 | SET | 551
1 | Supply and fixing of wooden board of size 3'x2'.5'indicating the layout of the Switch yard. | Electrical work | Sup &fix of board ind Switchyard layout | As per relevent standard specification | 1654 | EA | 1654
1 | Supply and Erection of Permanent Name Board of on 3'x4' steel sheetmounted on steel frame as described in Specification. | Electrical work | Sup 33/11kv S.S Permanent name board | As per relevent standard specification | 10238 | EA | 10238
1 | Supply of Digital clamp meter. | Electrical work | Supply of Digital clamp meter. | As per relevent standard specification | 2888 | EA | 2888
1 | Supply of Rechargeable LED torch light of Standard make. | Electrical work | Sup Rechargeable LED torch light. | As per relevent standard specification | 1733 | EA | 1733
1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box containing ‘D’Spanners from size 6 to 54, Hammer small and big size, Ring spanners from 6 to 28, Adjustable spanner, Pipe wrench, Cutting Plier, Nose plier, Tester, insulated Screw drive. | Electrical work | SupTaparia Tool kit complete as per Spec | As per relevent standard specification | 4925 | SET | 4925
1 | Supply and fixing of safety instructions/Substation operation instruction board | Electrical work | Sup& fix safety inst/SS Op. inst board | As per relevent standard specification | 2205 | EA | 2205
8 | Supply of 25 W LED lamp with fitting of philips make | Electrical work | S-25W LED fixture set | As per relevent standard specification | 3200 | EA | 25600
1 | Supply of Alluminum Ladder(20 feet) | Electrical work | S-10ft Aluminium Ladder | As per relevent standard specification | 1654 | EA | 1654
1 | Supply of Megger (2000 ohms, 0-2.5kv) | Electrical work | Supply of Earth megger (1000v) | As per relevent standard specification | 8085 | EA | 8085
4 | Supply of Earth Discharging Rod 10' length. | Electrical work | S-Earth Rod 8ft Long 3mm Thick | As per relevent standard specification | 1000 | EA | 4000
250 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 29375
66 | Supply of PG clamps for panther 2 bolted 800 A. | Electrical work | S-Al. alloy three bolted PG clamps 800A | As per relevent standard specification | 130 | EA | 8580
200 | Supply and Laying of 2 core/4 core cable includes excavation earth and back filling with sand and earth in alternate layers as shown in the sketch. The cable termination shall be made by providing proper size of lugs at both ends of the cable termination. | Electrical work | 33/11kv S.S laying of 2/4core for light | As per relevent standard specification | 50 | M | 10000
31 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 12625.99
8 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 2172.16
2 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip. | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 5440.68
10.61 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 6547.431
10.61 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 2344.81
10.61 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 1962.85
354 | Loading and unwinding of Panther conductor. | Electrical work | Load-Unwinding Panther conductor | As per relevent standard specification | 3 | M | 1062
354 | Unloading of Panther conductor. | Electrical work | Unload-Unwinding Panther conductor | As per relevent standard specification | 2 | M | 708
2 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | KI | 4
2 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | KI | 4
2 | Loading of 33KV Metal parts bag of 25 nos. | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 130
2 | Unloading of 33 KV Metal parts bag of 25 nos. | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 130
2 | Loading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | LOADING of 11kv Pin/Post/Solid Core Insu | As per relevent standard specification | 1 | KI | 2
2 | Unloading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | UNLOADING of 11kv Pin/Post/Solid Core In | As per relevent standard specification | 1 | KI | 2
700 | Loading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | Load-PVC Control Cable 10C | As per relevent standard specification | 1 | M | 700
700 | Unloading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | UnLoad-PVC Control Cable 10C | As per relevent standard specification | 1.02 | M | 714
1 | Loading of 3Ph 25KVA Distribution Transformer. | Electrical work | Load-3Ph 25KVA DTR | As per relevent standard specification | 252 | EA | 252
1 | UnLoading of 3Ph 25KVA Distribution Transformer. | Electrical work | UnLoad-3Ph 25KVA DTR | As per relevent standard specification | 202 | EA | 202
1 | Loading of 33/11 KV Current Transformers/ Potential Transformers. | Electrical work | LOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 165 | EA | 165
3 | Loading of 33 KV10 KA LAs Station type. | Electrical work | LOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 41 | EA | 123
3 | Unloading of 33 KV10 KA LAs Station type. | Electrical work | UNLOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 35 | EA | 105
9 | Loading of 11 KV10 KA LAs Line type. | Electrical work | LOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 288
9 | Unloading of 11 KV10 KA LAs Line type. | Electrical work | UNLOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 288
3 | Loading of 11 KV10 KA LAs Station type. | Electrical work | LOADING of 11 KV,10 KA LAs Station type | As per relevent standard specification | 32 | EA | 96
3 | Unloading of 11 KV10 KA LAs Station type. | Electrical work | UNLOADING of 11 KV,10 KA LAs Station typ | As per relevent standard specification | 32 | EA | 96
2 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 252
2 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 158
9 | loading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 720
9 | Unloading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 720
4 | Loading and Unloading of 12V/24V Battery Set. | Electrical work | Load/Unload-12V/24V Battery Set | As per relevent standard specification | 23 | EA | 92
1 | Erection of 11kv Potential Transformer sets complete including jumpering. The LV side of the PT shall be provided with proper fuse protection mounted in separate marshalling boxwith proper size cable glands etc. The box shall be mounted on the Substation structure. | Electrical work | Erection of 11kv three phase PT s | As per relevent standard specification | 800 | SET | 800
1 | Unloading of 33/11 KV Current Transformers/ Potential Transformers | Electrical work | UNLOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 128 | EA | 128
1 | Fixing of Distribution Box and Providing with proper Fuse protection system and reqired Cable Terminations at Station T/F LT side and AC/DC Panel and fixing meter. Power cable of adequate size shall be provided from station DTR to control room AC Panel. | Electrical work | Erection of LT distribution box | As per relevent standard specification | 1594.67 | EA | 1594.67
1 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply and fixing of PT Marshalling box | As per relevent standard specification | 1139.85 | EA | 1139.85
2 | Supply of Hand Gloves | Electrical work | Supply of Hand Gloves | As per relevent standard specification | 289 | SET | 578
2 | Supply of Safety Helmets of standard make | Electrical work | Supply of Safety Helmet of standard make | As per relevent standard specification | 231 | EA | 462
5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for First coat of 1st GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 11995.5
5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 1st coat of Aluminium | Electrical work | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 4680.5
20 | Supply & Providing of Panther T clamps. | Electrical work | Supply & Providing of Panther T clamps. | As per relevent standard specification | 320 | EA | 6400
5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for second coat of 2nd GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 7111.5
5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 2nd coat of Aluminium | Electrical work | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 2651
8.85 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 33 kv line | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 6770.25
15 | Excavation of Pole pits of size 0.76x0.9x1.95 Mts' for 12.5 mts spun Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAV. OF PIT 0.75 M x 0.9 M x 1.95 M | As per relevent standard specification | 720 | EA | 10800
103 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 72100
60 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0") | As per relevent standard specification | 1680 | EA | 100800
39 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 23400
15 | Erection of 12.5 Mtr spun pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Earth work | Erection of Spun pole 12.5Mt | As per relevent standard specification | 4115.7 | EA | 61735.5
15 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 75 x 8 mm MS Flat | Earth work | Fab Back clamps with 75 x 8 mm MS Flat | As per relevent standard specification | 31.62 | EA | 474.3
163 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 678940.64
39 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Earth work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 93600
36 | Formation of 33 kv cut points (Vertical/Horizantal) including fixing of Clamps and top cleat and fixing of pin insulator complete with necessary hard wear for stud locations excluding the cost of pit Excavation and the pole shall be numbered with colour paint and earthing. | Electrical work | Horizontal Cut point for 33 KV line | As per relevent standard specification | 1759.5 | EA | 63342
67.97 | Concreting the location after erection of 12.5/11 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.75X0.9X1.95 Mts)* 5 = 7.22 Cu.Mt and (0.75X0.75X2 Mts)* 54 = 60.75 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 447174.63
8.85 | Paving of the 100 sqmm AAA conductor and stringing duly arranging temporary guys, tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pin binding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Earth work | Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevent standard specification | 12600.06 | KM | 111510.531
220 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 25850
163 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 70411.11
39 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Earth work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 15884.31
6 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 1212
6 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 600
6 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip. | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 16322.04
2.015 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 1243.4565
2.015 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 445.315
2.015 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 372.775
87 | Loading of 33 KV Pin insulators | Electrical work | LOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | KI | 261
87 | Unloading of 33 KV Pin insulators | Electrical work | UNLOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | KI | 261
36 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | KI | 72
36 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | KI | 72
36 | Loading of 33KV Metal parts bag of 25 nos. | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 2340
36 | Unloading of 33 KV Metal parts bag of 25 nos. | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 2340
95 | Erection of 33 kv Stay set complete including fixing of bow ,fixing and binding of Eye bolt, Anchor rod, guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. | Electrical work | Assembly and erection of Stay set 33kv | As per relevent standard specification | 684.53 | SET | 65030.35
34.304 | Mass concreting with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for stay/stud locations .Using form boxes ( 0.45x0.45x1.265) *134= 34.304 cu mts | Civil work | Mass concreting of stay locations | As per relevent standard specification | 6579 | EA | 225686.016
95 | Excavation of Stay pits of size 0.45x0.45x1.265 Mts' for burying the anchor rod with anchor plate of stay sets including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits any and leveling the site with out any lead.In all soils with Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting | Electrical work | Exc Stay pit 0.45x0.45x1.265M Hard Soil | As per relevent standard specification | 1271.18 | EA | 120762.1
3.36 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 33 kv line | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 2570.4
21 | Excavation of Pole pits of size 0.76x0.9x1.95 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting | Earth work | EXCAV. OF PIT 0.75 M x 0.9 M x 1.95 M | As per relevent standard specification | 720 | EA | 15120
11 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 6600
30 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 21000
32 | Excavation of Stay pits of size 0.45x0.45x1.265 Mts' for burying the anchor rod with anchor plate of stay sets including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits any and leveling the site with out any lead.In all soils with Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting | Earth work | Exc Stay pit 0.45x0.45x1.265M Hard Soil | As per relevent standard specification | 1271.18 | EA | 40677.76
21 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Earth work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 87470.88
11 | Erection of 8.0 Mts PSCC Poles complete with necessary hard ware for yard lighting excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Earth work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 16500
30 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Earth work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 72000
17 | Formation of 11 kv cut points (Vertical/Horizantal) including fixing of 11 KV Cross arms,clamps, strain insulators sets complete with hardware and stays (Bows and Eye-bolts), Excluding the cost of pit Excavation and pole erection. The contractor has to supply GI Bolts and Nuts. | Electrical work | Formatn of Horiz Cut point for 11KV line | As per relevent standard specification | 1350 | EA | 22950
8.008 | Concreting the location after erection of 9.1/11 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.76X0.76X1.52 Mts)* 4 = 3.508 Cu.Mt and (0.75X0.75X2 Mts)* 4 = 4.5 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 52684.632
13.312 | Mass concreting with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for stay/stud locations .Using form boxes ( 0.45x0.45x1.265) *52= 34.304 cu mts | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 87579.648
1.01 | Paving of the conductor 55 Sqmm Single Circuit (3 Conductors) AAAC and stringing duly arranging temporary guys,tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pinbinding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing of 55sqmm 33/11kv Line 3 Cond | As per relevent standard specification | 8500 | KM | 8585
150 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 17625
1.271 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 280.891
1.271 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 235.135
185 | Loading 11KV Polymer Pin Insulator with GI pins | Electrical work | Load-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 185
185 | Unloading 11KV Polymer Pin Insulator with GI pins | Electrical work | Unload-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 185
1.271 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 746.7379
2 | Transport of VCB , Control pannels, current transformater, bosster etc, above 20 KM and upto 30 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs >20 & <30Km | As per relevent standard specification | 3691.38 | EA | 7382.76
2 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 404
2 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 200
11 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM. | Earth work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 2986.72
30 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Earth work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 12218.7
21 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Earth work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 9071.37
34 | Loading of 11 KV V - Cross arms | Electrical work | LOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 136
34 | Unloading of 11 KV V - Cross arms | Electrical work | UNLOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 136
10 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 480
10 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 480
16 | Loading of 11 KV Top fittings | Electrical work | LOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 16
16 | Unloading of 11 KV Top fittings | Electrical work | UNLOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 16
10 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | KI | 20
10 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | KI | 20
32 | Erection of 11 kv Stay set complete including fixing of bow, fixing and binding of Eye bolt,Anchor rod,guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. The contractor has to supply GI Bolts and Nuts. | Earth work | Assembly and erection of Stay set11kv&LT | As per relevent standard specification | 606.85 | SET | 19419.2
1.05 | Paving of the conductor 55 Sqmm double Circuit (6 Conductors) AAAC and stringing duly arranging temporary guys,tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pinbinding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing of 55sqmm 33/11kv Line 6 Cond | As per relevent standard specification | 16000 | KM | 16800
2 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 9000
8 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Electrical work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 4800
4 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 2800
8 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 19200
4 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 16661.12
7.88 | Concreting the location after erection of 9.1/11 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 51842.52
10 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 1175
0.68 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 150.28
0.68 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 125.8
0.68 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.51 | TO | 399.5068
8 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 3258.32
4 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 1727.88
1 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 48
1 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 48
1 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | KI | 2
1 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | KI | 2
4 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 13944
4 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.6M dia x 0.5 M height | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 4936.8
64 | Supply of earthing GI Flat 25X3 mm including material | Earth work | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 6720
2 | LOADING of 33 KV AB SWCH Con 400/800 A | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 252
2 | UNLOADING of 33 KV AB SWCH Con 400/800 A | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 158
4 | Erection of 11kV AB Switches 800/400 Amps includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 12800
8 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 940
0.274 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 220.99 | TO | 60.5513
0.274 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 50.69
0.274 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 160.9805
4 | Supply of C I earth pipe of size 50mm dia, 2 mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 50mm dia 2m long | As per relevent standard specification | 2441 | EA | 9764
8 | Loading/Unloading of C I earth pipe of size 80/50mm dia, 2 mtrs long for earth electrode | Electrical work | Load/Unload-CI pipe 80/50 mm dia 2mt L | As per relevent standard specification | 18 | EA | 144
4 | Providing of collar rings of 450mm dia at 4 pole structure | Electrical work | Collar/ Rings of 450mm dia | As per relevent standard specification | 260 | EA | 1040
40 | Supply of earthing GI Flat 25X3 mm including material | Electrical work | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 4200
4 | loading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 320
4 | Unloading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 320
4 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 2800
4 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 2400
4 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 16661.12
4 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 9600
8.008 | Concreting the location after erection of 9.1/11 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.76X0.76X1.52 Mts)* 4 = 3.508 Cu.Mt and (0.75X0.75X2 Mts)* 4 = 4.5 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 52684.632
0.7 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the ply and fabrication of 6mm base and top plate for Box pole to theRS Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | Electrical work | Fabrication of struc.with power drilling | As per relevent standard specification | 6852 | TO | 4796.4
5 | Erection of 33kV and 11kV Strung Bus with Panther (200Sqmm) ACSR Conductor: Erection of 33kV and 11kV Bus over the Substation structures with 200sqmm Panther ACSR conductor and giving Jumpers to connect the Switch gear by providing the suitable T clamps and round clamps suitable to Post type insulators & Insulators. | Electrical work | Stringing of bus with panther conductor | As per relevent standard specification | 327.68 | M | 1638.4
2 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 9000
1 | Erection of 33KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 33kv LA stn type incl earthing | As per relevent standard specification | 880 | SET | 880
4 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 13944
4 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 4936.8
25 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 2937.5
12 | Sup PG clamps for panther 2 bolted 600 A | Electrical work | SupPG clamps for panther 2 bolted 600 A | As per relevent standard specification | 100 | EA | 1200
2 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 252
2 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 158
0.89 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 549.219
0.89 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 196.69
0.89 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 164.65
4 | LOADING of CI Earth pipe upto 2.7 Mtr | Electrical work | LOADING of CI Earth pipe upto 2.7 Mtr | As per relevent standard specification | 29 | EA | 116
4 | UNLOADING of CI Earth pipe upto 2.7 Mtr | Electrical work | UNLOADING of CI Earth pipe upto 2.7 Mtr | As per relevent standard specification | 29 | EA | 116
16 | Hire-JCB to Level & Clear the Site | Civil work | Hire-JCB to Level & Clear the Site | As per relevent standard specification | 2165.7 | H | 34651.2
102.9 | Excavation in Ordinary Soil | Civil work | Excavation in Ordinary Soil | As per relevent standard specification | 366 | M3 | 37661.4
19.2 | PCC with 40mm Metal (1:4:8) | Civil work | PCC with 40mm Metal (1:4:8) | As per relevent standard specification | 4303 | M3 | 82617.6
132.6 | CRS Masonary CM(1:6) 2nd Sort | Civil work | CRS Masonary CM(1:6) 2nd Sort | As per relevent standard specification | 4257 | M3 | 564478.2
23.1 | Brick Masonary in CM(1:6) GFloor | Civil work | Brick Masonary in CM(1:6) GFloor | As per relevent standard specification | 8213 | M3 | 189720.3
667.6 | S&Filling with Borrowed Gravel | Civil work | S&Filling with Borrowed Gravel | As per relevent standard specification | 485 | M3 | 323786
5.9 | RCC Footing: M20Gr, Steel Centering | Civil work | RCC Footing: M20Gr, Steel Centering | As per relevent standard specification | 8552 | M3 | 50456.8
2.9 | RCC Column GF: M20Gr, Steel Centering | Civil work | RCC Column GF: M20Gr, Steel Centering | As per relevent standard specification | 11427 | M3 | 33138.3
2 | RCC Plinth Beam: M20Gr, Steel Centering | Civil work | RCC Plinth Beam: M20Gr, Steel Centering | As per relevent standard specification | 11169 | M3 | 22338
0.9 | RCC Lintel GF: M20Gr, Steel Centering | Civil work | RCC Lintel GF: M20Gr, Steel Centering | As per relevent standard specification | 11618 | M3 | 10456.2
13.5 | RCC Sunshade GF: M20Gr, Steel Centering | Civil work | RCC Sunshade GF: M20Gr, Steel Centering | As per relevent standard specification | 1229 | M2 | 16591.5
2.9 | RCC Roof Beam GF: M20Gr, Steel Centering | Civil work | RCC Roof Beam GF: M20Gr, Steel Centering | As per relevent standard specification | 11227 | M3 | 32558.3
10.2 | RCC Roof Slab GF: M20Gr, Steel Centering | Civil work | RCC Roof Slab GF: M20Gr, Steel Centering | As per relevent standard specification | 10741 | M3 | 109558.2
2.5 | Reinforcement Steel Fe 415/500 | Civil work | Reinforcement Steel Fe 415/500 | As per relevent standard specification | 72726 | TON | 181815
404.66 | Plastering 20mm (16mm+4mm)GFloor | Civil work | Plastering 20mm (16mm+4mm)GFloor | As per relevent standard specification | 434 | M2 | 175622.44
142.5 | Raised Pointing to CRS Masonary CM(1:3) | Civil work | Raised Pointing to CRS Masonary CM(1:3) | As per relevent standard specification | 98 | M2 | 13965
78.1 | Impervious Coat 20mm CM(1:3) GFloor | Civil work | Impervious Coat 20mm CM(1:3) GFloor | As per relevent standard specification | 462 | M2 | 36082.2
5.7 | S&F MT Wood Frame & Door-Laminate | Civil work | S&F MT Wood Frame & Door-Laminate | As per relevent standard specification | 6871 | M2 | 39164.7
5.76 | S&F Powder Coated Al Window | Civil work | S&F Powder Coated Al Window | As per relevent standard specification | 3572 | M2 | 20574.72
6.25 | S&F of MS Safety Grill | Civil work | S&F of MS Safety Grill | As per relevent standard specification | 2622 | M2 | 16387.5
39.2 | Polished Shabad Flooring 20mm CM(1:3) | Civil work | Polished Shabad Flooring 20mm CM(1:3) | As per relevent standard specification | 541 | M2 | 21207.2
10.7 | Polished Shabad Skirting CM(1:3) | Civil work | Polished Shabad Skirting CM(1:3) | As per relevent standard specification | 610 | M2 | 6527
32.5 | PCC with 40mm Metal (1:3:6) | Civil work | PCC with 40mm Metal (1:3:6) | As per relevent standard specification | 4582 | M3 | 148915
6.8 | PCC with 20mm Metal (1:2:4) | Civil work | PCC with 20mm Metal (1:2:4) | As per relevent standard specification | 5715 | M3 | 38862
49.5 | S&Spreading of 20mm HBG Metal | Civil work | S&Spreading of 20mm HBG Metal | As per relevent standard specification | 1618 | M3 | 80091
110 | S&F MS Security Fencing Mesh (2"X2") | Civil work | S&F MS Security Fencing Mesh (2"X2") | As per relevent standard specification | 2110 | M2 | 232100
10.55 | S&F MS Gate | Civil work | S&F MS Gate | As per relevent standard specification | 4676.9 | M2 | 49341.295
121 | Painting with OBD 2Coats+Primer | Civil work | Painting with OBD 2Coats+Primer | As per relevent standard specification | 115 | M2 | 13915
178.4 | Painting SnowCem/Apex 2 Coats+Primer | Civil work | Painting SnowCem/Apex 2 Coats+Primer | As per relevent standard specification | 205 | M2 | 36572
175.9 | Painting with SuryaCem of 3 Coat | Civil work | Painting with SuryaCem of 3 Coat | As per relevent standard specification | 73 | M2 | 12840.7
30 | S&F Conceal PVC Pipe 25mm dia in Slab | Civil work | S&F Conceal PVC Pipe 25mm dia in Slab | As per relevent standard specification | 90 | M | 2700
20 | S&F Conceal PVC Pipe 25mm dia in Wall | Civil work | S&F Conceal PVC Pipe 25mm dia in Wall | As per relevent standard specification | 93 | M | 1860
15 | S&F Modular Switch LP,FP,EFP for NRBuild | Civil work | S&F Modular Switch LP,FP,EFP for NRBuild | As per relevent standard specification | 602 | EA | 9030
2 | S&F Modular 3/2pin 6A Sockets | Civil work | S&F Modular 3/2pin 6A Sockets | As per relevent standard specification | 493 | EA | 986
2 | S&F Modular 3pin 16/6A Sockets | Civil work | S&F Modular 3pin 16/6A Sockets | As per relevent standard specification | 455 | EA | 910
4 | S&F Batten Holder | Civil work | S&F Batten Holder | As per relevent standard specification | 224 | EA | 896
4 | S&F 20W LED Retro Tube Light | Civil work | S&F 20W LED Retro Tube Light | As per relevent standard specification | 876.5 | EA | 3506
90 | S&R 2 of 14/0.3mm (1.0sqmm) (FR) | Civil work | S&R 2 of 14/0.3mm (1.0sqmm) (FR) | As per relevent standard specification | 49 | M | 4410
30 | S&R 2 of 36/0.3mm (2.5sqmm) (FR) | Civil work | S&R 2 of 36/0.3mm (2.5sqmm) (FR) | As per relevent standard specification | 100 | M | 3000
1 | S&F 8wySPNDB IP-20,10kA-6-32A SPMCB 4No | Civil work | S&F 8wySPNDB IP-20,10kA-6-32A SPMCB 4No | As per relevent standard specification | 5368 | EA | 5368
1 | Provd-Independent Earthing | Civil work | Provd-Independent Earthing | As per relevent standard specification | 5169 | EA | 5169
15 | S&R No.8 SWG Copper Wire | Civil work | S&R No.8 SWG Copper Wire | As per relevent standard specification | 153 | M | 2295
2 | S&F 1200mm (48'') Sweep Ceiling Fan | Civil work | S&F 1200mm (48'') Sweep Ceiling Fan | As per relevent standard specification | 2225 | EA | 4450
13.7 | Ceramic Tile Flooring 20mm CM(1:3) | Civil work | Ceramic Tile Flooring 20mm CM(1:3) | As per relevent standard specification | 949 | M2 | 13001.3
1 | S&F Orissa Pan WC 580mmx440mm | Civil work | S&F Orissa Pan WC 580mmx440mm | As per relevent standard specification | 2207 | EA | 2207
2 | S&F Floor Trap (Bell Mouth) 110mm | Civil work | S&F Floor Trap (Bell Mouth) 110mm | As per relevent standard specification | 269 | EA | 538
2 | S&F 90mm dia Plain Bend PVC/SWR Pipe | Civil work | S&F 90mm dia Plain Bend PVC/SWR Pipe | As per relevent standard specification | 84 | EA | 168
1 | S&F 75mm dia Door Bend PVC/SWR Pipe | Civil work | S&F 75mm dia Door Bend PVC/SWR Pipe | As per relevent standard specification | 81 | EA | 81
1 | S&F 150mmx100mm SWG Gully Trap | Civil work | S&F 150mmx100mm SWG Gully Trap | As per relevent standard specification | 749 | EA | 749
6 | S&F 110mm dia 3M 1Socket PVC/SWR Pipe | Civil work | S&F 110mm dia 3M 1Socket PVC/SWR Pipe | As per relevent standard specification | 428 | M | 2568
1 | S&F 4" dia PVC Cowl | Civil work | S&F 4" dia PVC Cowl | As per relevent standard specification | 23 | EA | 23
1 | Construct- 4' dia & 5' Ht Soak Pit | Civil work | Construct- 4' dia & 5' Ht Soak Pit | As per relevent standard specification | 4951 | EA | 4951
150 | S&F 22.20mm OD CPVC Pipe-SDR 11 | Civil work | S&F 22.20mm OD CPVC Pipe-SDR 11 | As per relevent standard specification | 417 | M | 62550
100 | S&F 28.60mm OD CPVC Pipe-SDR 11 | Civil work | S&F 28.60mm OD CPVC Pipe-SDR 11 | As per relevent standard specification | 514 | M | 51400
24 | S&F-15mm GM/Bronze Ball Valve | Civil work | S&F-15mm GM/Bronze Ball Valve | As per relevent standard specification | 230 | EA | 5520
1 | S&F-20mm GM/Bronze Ball Valve | Civil work | S&F-20mm GM/Bronze Ball Valve | As per relevent standard specification | 331 | EA | 331
2 | S&F-25mm GM/Bronze Ball Valve | Civil work | S&F-25mm GM/Bronze Ball Valve | As per relevent standard specification | 466 | EA | 932
4 | S&F-15mm Bib Tap 400gm Full turn | Civil work | S&F-15mm Bib Tap 400gm Full turn | As per relevent standard specification | 275 | EA | 1100
500 | S&F Polyethylene Water Storage Tank | Civil work | S&F Polyethylene Water Storage Tank | As per relevent standard specification | 10 | L | 5000
1 | Supply of Table 4'x2' with MS Frame | Civil work | Supply of Table 4'x2' with MS Frame | As per relevent standard specification | 4350 | EA | 4350
1 | Supply of S-Type Chair | Civil work | Supply of S-Type Chair | As per relevent standard specification | 4035 | EA | 4035
2 | Supply of PVC Chair | Civil work | Supply of PVC Chair | As per relevent standard specification | 1200 | EA | 2400
3 | S&F Glow Sign Board | Civil work | S&F Glow Sign Board | As per relevent standard specification | 3735 | M2 | 11205
1.35 | S&F MS Board | Civil work | S&F MS Board | As per relevent standard specification | 4545 | M2 | 6135.75
71.42 | S&Filling with Borrowed Stone Dust | Civil work | S&Filling with Borrowed Stone Dust | As per relevent standard specification | 1028 | M3 | 73419.76
7.3 | S&F RCC Hume Pipe of 450mm dia | Civil work | S&F RCC Hume Pipe of 450mm dia | As per relevent standard specification | 1345 | M | 9818.5
150 | S&F RCC Fencing Pole 0.115mx0.115mx2.7m | Civil work | S&F RCC Fencing Pole 0.115mx0.115mx2.7m | As per relevent standard specification | 1443 | EA | 216450
25 | S&F RCC Fencing Pole 0.1mx0.1mx1.8m | Civil work | S&F RCC Fencing Pole 0.1mx0.1mx1.8m | As per relevent standard specification | 1299 | EA | 32475
300 | S&F Barbed Wire 8H & 2Cross | Civil work | S&F Barbed Wire 8H & 2Cross | As per relevent standard specification | 260 | M | 78000
1 | Provd-Supply of Electricity to Site | Civil work | Provd-Supply of Electricity to Site | As per relevent standard specification | 5678 | EA | 5678
1 | Geophysical Investgation Charges | Civil work | Geophysical Investgation Charges | As per relevent standard specification | 7000 | EA | 7000
90 | Drilling-165mm Bore Well 0 to 90M | Civil work | Drilling-165mm Bore Well 0 to 90M | As per relevent standard specification | 336 | M | 30240
30 | Drill-165mm Bore Well 90M to 120M | Civil work | Drill-165mm Bore Well 90M to 120M | As per relevent standard specification | 389 | M | 11670
30 | Drill-165mm Bore Well 120M to 150M | Civil work | Drill-165mm Bore Well 120M to 150M | As per relevent standard specification | 407 | M | 12210
30 | S&F 160mm dia PVC Casing | Civil work | S&F 160mm dia PVC Casing | As per relevent standard specification | 1650 | M | 49500
1 | S&E SP SubMrsbl Pumpset 2.0HP 30 Stages | Civil work | S&E SP SubMrsbl Pumpset 2.0HP 30 Stages | As per relevent standard specification | 34894 | EA | 34894
60 | S&R 3C 2.5sqmm Flat Copper Cable | Civil work | S&R 3C 2.5sqmm Flat Copper Cable | As per relevent standard specification | 210 | M | 12600
1 | S&E D.O.L Starter 250V Single Phase | Civil work | S&E D.O.L Starter 250V Single Phase | As per relevent standard specification | 2400 | EA | 2400
1 | Supply & ixing of Flange Clamps | Civil work | Supply & ixing of Flange Clamps | As per relevent standard specification | 191 | EA | 191
178 | S&F-HDPE Pipe 40mm dia 16kg/sqcm-SDR 9 | Civil work | S&F-HDPE Pipe 40mm dia 16kg/sqcm-SDR 9 | As per relevent standard specification | 155 | M | 27590
173.5 | Seigniorage Charges - Sand | Civil work | Seigniorage Charges - Sand | As per relevent standard specification | 40 | M3 | 6940
151.5 | Seigniorage Charges - Metal | Civil work | Seigniorage Charges - Metal | As per relevent standard specification | 97.5 | M3 | 14771.25
667.6 | Seigniorage Charges - Gravel | Civil work | Seigniorage Charges - Gravel | As per relevent standard specification | 30 | M3 | 20028