## Sheet1
Name of the work: Providing of alternate source to 33/11 KV Laxmisagar SS from 33KV Mudimanikyam feeder emanating from 132/33 KV Singur EHT Sub-Station by erection of new 33KV interlinking SCOH line with 100sq.mm AAA conductor for a distance of 4.99KM in Pulkal Section of Jogipet Sub-Division of Jogipet Division in Sangareddy Circle(WBS NO.T-2531-90-06-01-02-002)
S NO | SSR CODES | Estimate Quantity (Only figures) | Item Detailed Specification Description | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SWR22092 | 4.99 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 33 kv line | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 3817.35
2 | SWR10107 | 38 | Excavation of Pole pits of size 0.76x0.76x1.52 Mts' for 9.1 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock not Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 26600
3 | SWR11040 | 25 | Excavation of Pole pits of size 0.75x0.9x1.95 Mts' for 11.0 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils with Hard gravel Hard Murram, Disintegrated Rock, Hard rock not requiring blasting. | Earth work | Ex of Hard pit w/o blast 0.75X0.9X1.95M | As per relevent standard specification | 883.58 | EA | 22089.5
4 | SWR10978 | 108 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit exc | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 449850.24
5 | SWR10343 | 38 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit ex | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 91200
6 | SWR10981 | 18 | Formation of 33 kv cut points (Vertical/Horizantal) including fixing of Clamps and top cleat and fixing of pin insulator complete with necessary hard wear for stud locations excluding the cost of pit Excavation and the pole shall be numbered with colour | Electrical work | Horizontal Cut point for 33 KV line | As per relevent standard specification | 1759.5 | EA | 31671
7 | SWR10356 | 54 | Concreting the location after erection of 11.0 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.75X0.75X2 Mts)* 48 = 54 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 355266
8 | SWR10366 | 4.99 | Paving of the 100 sqmm AAA conductor and stringing duly arranging temporary guys, tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pin binding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be b | Earth work | Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevent standard specification | 12600.06 | KM | 62874.2994
9 | SMR11488 | 200 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 23500
10 | SWR11180 | 108 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 46652.76
11 | SWR20308 | 38 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 15477.02
12 | SWR10191 | 3 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 606
13 | SWR10509 | 3 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 300
14 | SWR11860 | 3 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip. | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 8161.02
15 | SWR10150 | 1.05 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 647.955
16 | SWR10211 | 36 | Loading of 33 KV Pin insulators | Electrical work | LOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | KI | 108
17 | SWR10529 | 36 | Unloading of 33 KV Pin insulators | Electrical work | UNLOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | KI | 108
18 | SWR12416 | 12 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | KI | 24
19 | SWR10631 | 12 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | KI | 24
20 | SWR10618 | 5 | Loading of 33KV Metal parts bag of 25 nos. | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 325
21 | SWR10632 | 5 | Unloading of 33 KV Metal parts bag of 25 nos. | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 325
22 | SWR10354 | 10 | Erection of 33 kv Stay set complete including fixing of bow ,fixing and binding of Eye bolt, Anchor rod, guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. | Electrical work | Assembly and erection of Stay set 33kv | As per relevent standard specification | 684.53 | SET | 6845.3
23 | SWR21190 | 10 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 5200
24 | SWR10319 | 40 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 75 x 8 mm MS Flat | Earth work | Fab Back clamps with 75 x 8 mm MS Flat | As per relevent standard specification | 31.62 | EA | 1264.8
25 | SWR10378 | 108 | Numbering of poles incl. cost of paint | Electrical work | Numbering of poles incl. cost of paint | As per relevent standard specification | 32 | EA | 3456
26 | SWR10356 | 2.56 | Concreting the location after erection of 11.0 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for stay set location .Using form boxes (0.45X0.45X1.265 Mts)* 10 = 2.56 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 16842.24
27 | SWR10108 | 83 | Excavation of Pole pits of size 0.75x0.9x1.95 Mts' for 11.0 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock not requiring blasting. | Earth work | EXCAV. OF PIT 0.75 M x 0.9 M x 1.95 M | As per relevent standard specification | 720 | EA | 59760
28 | SWR10392 | 2 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper l | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 9000
29 | SWR10107 | 12 | Excavation of Pole pits of size 0.75x0.9x1.95 Mts' for 11.0 mts/9.1mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock not Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 8400
30 | SWR10978 | 4 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit exc | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 16661.12
31 | SWR11083 | 8 | Erection of 9.1 Mts long PSCC pole for strurt in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical work | Erec of 9.1 Mts PSCC poles for stuts | As per relevent standard specification | 2400 | EA | 19200
32 | SWR10356 | 8.54 | Concreting the location after erection of 11.0 mt /9.1mts pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.75X0.75X2 Mts)*4 and (0.6x0.6x1.5mts)*8 = 8.54 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 56184.66
33 | SMR11488 | 15 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 1762.5
34 | SWR10206 | 0.8 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 176.8
35 | SWR10524 | 0.8 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 148
36 | SWR10134 | 0.8 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.53 | TO | 470.024
37 | SWR11180 | 4 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 1727.88
38 | SWR20308 | 8 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 3258.32
39 | SWR12416 | 2 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | KI | 4
40 | SWR10631 | 2 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | KI | 4
41 | SMR11482 | 4 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 13944
42 | SWR10357 | 4 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Ben | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 4936.8
43 | SMR11485 | 60 | Supply of earthing GI Flat 25X3 mm including material | Earth work | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 6300
44 | SWR10239 | 2 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 252
45 | SWR10557 | 2 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 158
46 | SMR11488 | 20 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 2350
47 | SWR10206 | 0.6 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 132.6
48 | SWR10524 | 0.6 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 111
49 | SWR12416 | 2 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | KI | 4
50 | SWR10631 | 2 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | KI | 4
51 | SWR10618 | 2 | Loading of 33KV Metal parts bag of 25 nos. | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 130
52 | SWR10632 | 2 | Unloading of 33 KV Metal parts bag of 25 nos. | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 130
53 | SWR10884 | 8 | Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary | Electrical work | Conn. of equip/bus single zebra/panther | As per relevent standard specification | 224 | EA | 1792
54 | SWR10392 | 4 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper l | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 18000
55 | SMR11481 | 4 | Supply of CI earth pipe 100 mm dia, 2mt long thickness 10mm with flange as per specication | Electrical work | S-CI Pipe earthing 100mm dia 2m long | As per relevent standard specification | 2829 | EA | 11316
56 | SWR10357 | 4 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Ben | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 4936.8
57 | SWR10239 | 4 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 504
58 | SWR10557 | 4 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 316
59 | SWR10421 | 18 | Fixing of T clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) | Electrical work | Fixing of T- clamp | As per relevent standard specification | 116 | EA | 2088
60 | SWR10424 | 24 | Fixing of Pad clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) | Electrical work | Fixing of Pad clamps for AB Switch | As per relevent standard specification | 116 | EA | 2784
61 | SWR20557 | 6 | Erection of post type insulators | Electrical work | Erection of post type insulators | As per relevent standard specification | 50 | EA | 300
62 | SWR10210 | 1 | LOADING of 33 KV Post insulator | Electrical work | LOADING of 33 KV Post insulator | As per relevent standard specification | 2 | KI | 2
63 | SWR10528 | 1 | UNLOADING of 33 KV Post insulator | Electrical work | UNLOADING of 33 KV Post insulator | As per relevent standard specification | 1 | KI | 1
Total: | [8 empty] | 1420484.9884
18 % GST on labour: | [8 empty] | 255687.2979
Grand Total: | [8 empty] | 1676172.2863