## T-2532-07-05-01-03-002
Schedule for bifurcation of the existing 11KV AGL Bowrampet feeder emanating from 33/11KV DP Pally SS-I by laying of 1.28KM 11KV 3X185sq.mm XLPE UG cable (Double Run) from 33/11KV DP Pally SS-I along with bay extension & erection of 1No. 11KV VCB at the same SS in DP Pally Section of Shapurnagar Sub-Division in Jeedimetla Division in Medchal Circle under T&D Improvements to original works (Summer Action Plan-2026). WBS NO.T-2532-07-05-01-03-002
11 UG Cable Material
Sl.No. | SSR CODES | Estimate Quantity (Only figures) | Particulars | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item Short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SMR40081 | 40 | Cost of Pipes and slabs Supply of 6" B class GI pipe | Supply | Supply of work | As per relevent standard specification | 1344 | M | 53760
2 | SWR11982 | 1130 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet,3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,Along the CC / BT multi layer road requiring compressor. 11 KV 3x185 Sqmm Cable | Excavation | Excavation of work | As per relevent standard specification | 1264.64 | M | 1429043.2
3 | SWR12006 | 20 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)11 KV 3x185 Sqmm Cable | Erection | Erection of work | As per relevent standard specification | 243.53 | M | 4870.6
4 | SWR10390 | 4 | UG Cables Joints : Making of Outdoor/Indoor End Termination.Making 11 KV 3x185 Sqmm Cable Out Door/Indoor end termination | Erection | Erection of work | As per relevent standard specification | 2370.63 | EA | 9482.52
5 | SWR11230 | 10 | Const. of plinth for mount. new 5Way RMUs | Erection | Erection of work | As per relevent standard specification | 1024 | DR | 10240
6 | SWR11231 | 10 | Erection of 11KV 5 Way RMU | Erection | Erection of work | As per relevent standard specification | 1024 | DR | 10240
7 | SWR11862 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Above 20 Km and upto 30 Km with Lorry for each trip | LOADING | LOADING of work | As per relevent standard specification | 3691.38 | EA | 18456.9
8 | SWR11171 | 4 | UNLOADING of 11KV 5 Way RMU | UNLOADING | UNLOADING of work | As per relevent standard specification | 6 | EA | 24
9 | SWR11152 | 4 | Erection of OH Lines including AB Cable (33KV, 11KV, LT)S-Danger Sticker for RMU | Erection | Erection of work | As per relevent standard specification | 4 | EA | 16
10 | SWR11172 | 10 | Loading of -11/33KV XLPE UG Cable for all sizes | LOADING | LOADING of work | As per relevent standard specification | 8 | EA | 80
11 | SWR11153 | 10 | Unloading of - 11/33KV XLPE UG Cable all sizes | UNLOADING | UNLOADING of work | As per relevent standard specification | 4 | EA | 40
12 | SMR11482 | 5 | Erection of Equipment. Supply of earthing pipe with materials.CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Erection | Erection of work | As per relevent standard specification | 3486 | EA | 17430
13 | SWR10357 | 5 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Erection | Erection of work | As per relevent standard specification | 1234.2 | EA | 6171
14 | SWR10359 | 5 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Erection | Erection of work | As per relevent standard specification | 386 | EA | 1930
15 | SMR11485 | 45 | Supply of earthing pipe with materials. GI Flat 25X3 mm | Supply | Supply of work | As per relevent standard specification | 105 | KG | 4725
16 | SWR12125 | 75 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete | Erection | Erection of work | As per relevent standard specification | 14.03 | M | 1052.25
17 | SMR11488 | 50 | Supply of earthing pipe with materials.GI Bolts & Nuts etc | Supply | Supply of work | As per relevent standard specification | 117.5 | KG | 5875
18 | SWR10320 | 20 | Fabrication of materials including 2 coats of Red oxide painting.Back clamps with 50 x 6 mm MS Flat | Erection | Erection of work | As per relevent standard specification | 16 | EA | 320
19 | SMR40078 | 150 | Cost of Pipes and slabs.Supply of 150 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | Supply | Supply of work | As per relevent standard specification | 303 | M | 45450
20 | SWR11990 | 150 | Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) 11 KV 3x185 Sqmm Cable | Erection | Erection of work | As per relevent standard specification | 1449.06 | M | 217359
21 | SWR10385 | 10 | UG Cables Joints :Making of Straight through joints11 KV 3x185 Sqmm Cable | Erection | Erection of work | As per relevent standard specification | 3725.45 | EA | 37254.5
22 | SWR10988 | 1280 | Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable,placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Laying of 2nd cable in excavated trench | Erection | Erection of work | As per relevent standard specification | 204.1 | M | 261248
Schedule Cost. (Excluding GST) | [8 empty] | 2135067.97
11KV BAY and VCB
1 | SWR10461 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc. 11 KV VCB with Control Panel | Erection | Erection of work | As per relevent standard specification | 12000 | EA | 12000
2 | SMR11482 | 5 | Supply of earthing pipe with materials.CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Supply | Supply of work | As per relevent standard specification | 3486 | EA | 17430
3 | SWR11879 | 500 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Erection | Erection of work | As per relevent standard specification | 27 | M | 13500
4 | SMR11488 | 100 | Erection of Equipment Supply of earthing pipe with materials.GI Bolts & Nuts etc | Erection | Erection of work | As per relevent standard specification | 117.5 | KG | 11750
5 | SWR10942 | 1 | Testing of Sub-Station Equipment Wirring, commissioning and testing of Outdoor Sub-station switchgear duly conducting the pre commissioning test as per relevent standards & issue of certificate by CEIG authorised testing Engineer | Erection | Erection of work | As per relevent standard specification | 1825 | EA | 1825
6 | SWR10238 | 2 | LOADING of 11 KV AB SWCH Con 200/400 A | LOADING | LOADING of work | As per relevent standard specification | 80 | EA | 160
7 | SMR40025 | 6 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961)Supply of Alluminum PT clamps conforming to A6 of IS 617, with hot dip galvanised bolts and nuts suitable for single zebra / Panther | Supply | Supply of work | As per relevent standard specification | 368 | EA | 2208
8 | SMR40070 | 1 | 33/11KV Sub-Station Supply of Danger boards with clamps | Supply | Supply of work | As per relevent standard specification | 116 | EA | 116
9 | SWR10917 | 15 | Removal of existing conductor, jumpers and restringing of line with new conductor size and double jumpering and also replacement of damage insulators, cross arms etc. Complete.Labour for Fixing of all types of clamps | Erection | Erection of work | As per relevent standard specification | 65 | EA | 975
10 | SWR10393 | 2 | Erection of AB Switch and aligment complete 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Erection | Erection of work | As per relevent standard specification | 3200 | EA | 6400
11 | SWR11861 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators,transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Above 10 Km and upto 20 Km with Lorry for each trip | Erection | Erection of work | As per relevent standard specification | 3299.7 | EA | 3299.7
12 | SWR10199 | 1 | LOADING of 11 KV VCBs&Panel boards | LOADING | LOADING of work | As per relevent standard specification | 1024 | EA | 1024
13 | SWR10517 | 1 | UNLOADING of 11 KV VCBs&Panel boards | UNLOADING | UNLOADING of work | As per relevent standard specification | 1044.48 | EA | 1044.48
14 | SWR10556 | 2 | UNLOADING of 11 KV AB SWCH Con 200/400 A | UNLOADING | UNLOADING of work | As per relevent standard specification | 80 | EA | 160
15 | SWR11040 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Excavation | Excavation of work | As per relevent standard specification | 990.68 | EA | 1981.36
16 | SWR10206 | 1.3 | LOADING of MS Channel,Angles,Flats&Rods | LOADING | LOADING of work | As per relevent standard specification | 221 | TO | 287.3
17 | SWR10524 | 1.3 | UNLOADING of MS Channel,Angles,Flats&Rod | UNLOADING | UNLOADING of work | As per relevent standard specification | 185 | TO | 240.5
18 | SWR10265 | 3 | LOADING of 11 KV, 10 KA LAs Line type | LOADING | LOADING of work | As per relevent standard specification | 32 | EA | 96
19 | SWR10583 | 3 | UNLOADING of 11 KV, 10 KA LAs Line type | UNLOADING | UNLOADING of work | As per relevent standard specification | 32 | EA | 96
20 | SWR11701 | 500 | Loading of - PVC Control Cable 10C | LOADING | LOADING of work | As per relevent standard specification | 1 | M | 500
21 | SWR11712 | 500 | UnLoading of - PVC Control Cable 10C | UNLOADING | UNLOADING of work | As per relevent standard specification | 1.02 | M | 510
22 | SWR11220 | 100 | Loading of Unwinding Panther conductor | LOADING | LOADING of work | As per relevent standard specification | 3 | M | 300
23 | SWR11221 | 100 | Unloading of - Unwinding Panther conductor | UNLOADING | UNLOADING of work | As per relevent standard specification | 2 | M | 200
24 | SWR10307 | 120 | Drilling of holes upto 20 mm dia using power drills.MS Channel, Angles and flat | Erection | Erection of work | As per relevent standard specification | 4 | EA | 480
25 | SWR10359 | 5 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Erection | Erection of work | As per relevent standard specification | 386 | EA | 1930
26 | SWR10868 | 0.8 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels,R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Erection | Erection of work | As per relevent standard specification | 6852 | TO | 5481.6
27 | SWR21241 | 1 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Erection | Erection of work | As per relevent standard specification | 507 | EA | 507
28 | SMR11915 | 6 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. | Supply | Supply of work | As per relevent standard specification | 2055 | SET | 12330
29 | SWR11890 | 0.062 | Mass Concreting for pole Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Erection | Erection of work | As per relevent standard specification | 3893.06 | M3 | 241.37
30 | SMR40011 | 9 | Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . | Supply | Supply of work | As per relevent standard specification | 299 | EA | 2691
31 | SMR22473 | 6 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961)Supply of I-Bolts | Supply | Supply of work | As per relevent standard specification | 294 | EA | 1764
32 | SMR40009 | 0.8 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete.Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Erection | Erection of work | As per relevent standard specification | 2181 | TO | 1744.8
33 | SWR10877 | 0.8 | Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Erection | Erection of work | As per relevent standard specification | 851 | TO | 680.8
34 | SMR40010 | 0.8 | *)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Erection | Erection of work | As per relevent standard specification | 1293 | TO | 1034.4
35 | SWR10879 | 0.8 | (*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Erection | Erection of work | As per relevent standard specification | 482 | TO | 385.6
36 | SWR10920 | 42.55 | Laying of earth mat including excavation of trenches of depth 600mm, welding,connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication.75x 8mm MS Flat / GI Flat | Erection | Erection of work | As per relevent standard specification | 65 | RMT | 2765.75
37 | SWR10919 | 125 | Fabrication and connecting to risers from earth mat to structures, equipment,marshalling boxes, electrical panels, PLCC panels, fencing posts etc.M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Erection | Erection of work | As per relevent standard specification | 41 | RMT | 5125
38 | SWR12510 | 100 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Erection | Erection of work | As per relevent standard specification | 27 | EA | 2700
39 | SWR12331 | 2 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Erection | Erection of work | As per relevent standard specification | 146.63 | EA | 293.26
40 | SWR10881 | 2 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Erection | Erection of work | As per relevent standard specification | 142 | EA | 284
41 | SWR10860 | 5.5 | Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | Supply | Supply of work | As per relevent standard specification | 2113 | M3 | 11621.5
42 | SWR10743 | 2 | Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of coping with two coats of white cement (including cost of paint) | Erection | Erection of work | As per relevent standard specification | 686 | EA | 1372
43 | SWR10357 | 10 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Erection | Erection of work | As per relevent standard specification | 1234.2 | EA | 12342
44 | SMR40080 | 12 | Cost of Pipes and slabs. Supply of 4" B class GI pipe | Supply | Supply of work | As per relevent standard specification | 800 | M | 9600
45 | SMR11480 | 5 | Supply of earthing pipe with materials.GI eath pipe with 40 mm dia,3mm thcikness with 2.0 M Length | Supply | Supply of work | As per relevent standard specification | 698 | EA | 3490
46 | SMR11485 | 50 | Supply of earthing pipe with materials.GI Flat 25X3 mm | Supply | Supply of work | As per relevent standard specification | 105 | KG | 5250
47 | SWR10356 | 2.1 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Erection | Erection of work | As per relevent standard specification | 6579 | M3 | 13815.9
48 | SWR10522 | 1 | UNLOADING of R.S. Joists 175 x 85 mm | UNLOADING | UNLOADING of work | As per relevent standard specification | 50 | EA | 50
49 | SWR10204 | 1 | LOADING of R.S. Joists 175 x 85 mm | LOADING | LOADING of work | As per relevent standard specification | 76 | EA | 76
50 | SWR10264 | 3 | LOADING of 11 KV,10 KA LAs Station type | LOADING | LOADING of work | As per relevent standard specification | 32 | EA | 96
51 | SWR10582 | 3 | UNLOADING of 11 KV,10 KA LAs Station typ | UNLOADING | UNLOADING of work | As per relevent standard specification | 32 | EA | 96
52 | SWR20863 | 2 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation.5 Mts RS Joist (Bit) Pole including fixing of Pole Mounted Box | Erection | Erection of work | As per relevent standard specification | 1044.23 | EA | 2088.46
53 | SWR10348 | 2 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation.R.S. Joists 150 x 150 mm | Erection | Erection of work | As per relevent standard specification | 1952.61 | EA | 3905.22
54 | SWR10205 | 2 | LOADING of RSJoists150 x 150 mm/RailPole | LOADING | LOADING of work | As per relevent standard specification | 176 | EA | 352
55 | SWR10523 | 2 | UNLOADING of RSJoists150 x150 mm/RailPol | UNLOADING | UNLOADING of work | As per relevent standard specification | 107 | EA | 214
56 | SWR10105 | 2 | Excavation of pits in all soils except hard rock requiring blasting.8.0Mtrs PSCC Poles - 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | Excavation | Excavation of work | As per relevent standard specification | 650 | EA | 1300
57 | SWR20768 | 3.888 | Excavation of pits in hard rock requiring blasting. (other than SS)Earth work excavation of in all soils except hard rock requiring blasting. | Excavation | Excavation of work | As per relevent standard specification | 345 | M3 | 1341.36
58 | SWR10732 | 1 | Con of Plinth for 11kv VCB 1.8x1.8x0.75m | Erection | Erection of work | As per relevent standard specification | 27629 | EA | 27629
59 | SWR10397 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc.11 KV LAS station type including earthing | Erection | Erection of work | As per relevent standard specification | 559 | SET | 559
60 | SWR10398 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc.11 KV LAS line type including earthing | Erection | Erection of work | As per relevent standard specification | 505 | SET | 505
Schedule Cost. (Excluding GST) | [8 empty] | 212245.36
|  |  | Schedule Cost. (Excluding GST) | 2347313.33
|  |  | GST@18% | 422516.3994
|  |  | Schedule Cost Total | 2769829.7294

## T-2532-07-05-01-03-003
E-Procurement schedule for bifurcation of existing 11KV Gandimaisamma feeder emanating from 33/11KV DP Pally SS I by laying of 1.07KM 11KV3X185 sq.mm XLPE UG cable (Double Run) from 33/11KV DP Pally SS I on existing VCB at DP Pally SS I in DP Pally Section of Shapurnagar Sub-Division in Jeedimetla Division in Medchal Circle under T&D Improvement to original Works Summer action plan 2026. WBS NO.T-2532-07-05-01-03-003
11 UG Cable Material
Sl.No. | SSR CODES | Estimate Quantity (Only figures) | Particulars | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item Short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SMR40081 | 24 | Cost of Pipes and slabs Supply of 6" B class GI pipe | Supply | Supply of work | As per relevent standard specification | 1344 | M | 32256
2 | SWR11982 | 950 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet,3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,Along the CC / BT multi layer road requiring compressor. 11 KV 3x185 Sqmm Cable | Excavation | Excavation of work | As per relevent standard specification | 1264.64 | M | 1201408
3 | SWR12006 | 30 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)11 KV 3x185 Sqmm Cable | Erection | Erection of work | As per relevent standard specification | 243.53 | M | 7305.9
4 | SWR10390 | 4 | UG Cables Joints : Making of Outdoor/Indoor End Termination.Making 11 KV 3x185 Sqmm Cable Out Door/Indoor end termination | Erection | Erection of work | As per relevent standard specification | 2370.63 | EA | 9482.52
5 | SWR11230 | 9 | Const. of plinth for mount. new 5Way RMUs | Erection | Erection of work | As per relevent standard specification | 1024 | DR | 9216
6 | SWR11231 | 9 | Erection of 11KV 5 Way RMU | Erection | Erection of work | As per relevent standard specification | 1024 | DR | 9216
7 | SWR11862 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Above 20 Km and upto 30 Km with Lorry for each trip | Transport | Transport of work | As per relevent standard specification | 3691.38 | EA | 14765.52
8 | SWR11171 | 4 | Loading of 11/33 KV IN/OUT door kits | LOADING | LOADING of work | As per relevent standard specification | 6 | EA | 24
9 | SWR11152 | 4 | Un-loading of 11/33 KV IN/OUT door kits | UNLOADING | UNLOADING of work | As per relevent standard specification | 4 | EA | 16
10 | SWR11172 | 8 | Loading of -11/33KV XLPE UG Cable for all sizes | LOADING | LOADING of work | As per relevent standard specification | 8 | EA | 64
11 | SWR11153 | 8 | Unloading of - 11/33KV XLPE UG Cable all sizes | UNLOADING | UNLOADING of work | As per relevent standard specification | 4 | EA | 32
12 | SMR11488 | 30 | Supply of earthing pipe with materials.GI Bolts & Nuts etc | Supply | Supply of work | As per relevent standard specification | 117.5 | KG | 3525
13 | SWR10320 | 20 | Fabrication of materials including 2 coats of Red oxide painting.Back clamps with 50 x 6 mm MS Flat | Fabrication | Fabrication of work | As per relevent standard specification | 16 | EA | 320
14 | SMR40078 | 120 | Cost of Pipes and slabs.Supply of 150 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | Supply | Supply of work | As per relevent standard specification | 303 | M | 36360
15 | SWR11990 | 120 | Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) 11 KV 3x185 Sqmm Cable | Erection | Erection of work | As per relevent standard specification | 1449.06 | M | 173887.2
16 | SWR10385 | 8 | UG Cables Joints :Making of Straight through joints11 KV 3x185 Sqmm Cable | Supply | Supply of work | As per relevent standard specification | 3725.45 | EA | 29803.6
17 | SWR10393 | 1 | Erection of AB Switch and aligment complete 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Erection | Erection of work | As per relevent standard specification | 3200 | EA | 3200
18 | SWR10343 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation 9.1 M long PSCC pole | Erection | Erection of work | As per relevent standard specification | 2400 | EA | 2400
19 | SWR10107 | 1 | Excavation of pits in all soils except hard rock requiring blasting.9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | Excavation | Excavation of work | As per relevent standard specification | 700 | EA | 700
20 | SWR10356 | 0.54 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Erection | Erection of work | As per relevent standard specification | 6579 | M3 | 3552.66
21 | SWR20308 | 1 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)9.1 Mtrs long PSCC Poles | Erection | Erection of work | As per relevent standard specification | 407.29 | EA | 407.29
22 | SWR10988 | 1070 | Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable,placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Laying of 2nd cable in excavated trench | Excavation | Excavation of work | As per relevent standard specification | 204.1 | M | 218387
Schedule Cost. (Excluding GST) | [8 empty] | 1756328.69
11KV BAY and VCB
1 | SWR10461 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc. 11 KV VCB with Control Panel | Erection | Erection of work | As per relevent standard specification | 12000 | EA | 12000
2 | SMR11482 | 3 | Supply of earthing pipe with materials.CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Earthing | Earthing Of work | As per relevent standard specification | 3486 | EA | 10458
3 | SMR11488 | 50 | Erection of Equipment Supply of earthing pipe with materials.GI Bolts & Nuts etc | Erection | Erection of work | As per relevent standard specification | 117.5 | KG | 5875
4 | SWR10238 | 2 | LOADING of 11 KV AB SWCH Con 200/400 A | LOADING | LOADING of work | As per relevent standard specification | 80 | EA | 160
5 | SMR40025 | 6 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961)Supply of Alluminum PT clamps conforming to A6 of IS 617, with hot dip galvanised bolts and nuts suitable for single zebra / Panther | Supply | Supply of work | As per relevent standard specification | 368 | EA | 2208
6 | SMR40070 | 1 | 33/11KV Sub-Station Supply of Danger boards with clamps | Supply | Supply of work | As per relevent standard specification | 116 | EA | 116
7 | SWR10917 | 12 | Removal of existing conductor, jumpers and restringing of line with new conductor size and double jumpering and also replacement of damage insulators, cross arms etc. Complete.Labour for Fixing of all types of clamps | Erection | Erection of work | As per relevent standard specification | 65 | EA | 780
8 | SWR10393 | 2 | Erection of AB Switch and aligment complete 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Erection | Erection of work | As per relevent standard specification | 3200 | EA | 6400
9 | SWR10556 | 2 | UNLOADING of 11 KV AB SWCH Con 200/400 A | UNLOADING | UNLOADING of work | As per relevent standard specification | 80 | EA | 160
10 | SWR10206 | 0.7 | LOADING of MS Channel,Angles,Flats&Rods | LOADING | LOADING of work | As per relevent standard specification | 221 | TO | 154.7
11 | SWR10524 | 0.7 | UNLOADING of MS Channel,Angles,Flats&Rod | UNLOADING | UNLOADING of work | As per relevent standard specification | 185 | TO | 129.5
12 | SWR10265 | 3 | LOADING of 11 KV, 10 KA LAs Line type | LOADING | LOADING of work | As per relevent standard specification | 32 | EA | 96
13 | SWR10583 | 3 | UNLOADING of 11 KV, 10 KA LAs Line type | UNLOADING | UNLOADING of work | As per relevent standard specification | 32 | EA | 96
14 | SWR11220 | 45 | Loading of Unwinding Panther conductor | LOADING | LOADING of work | As per relevent standard specification | 3 | M | 135
15 | SWR11221 | 45 | Unloading of Unwinding Panther conductor | UNLOADING | UNLOADING of work | As per relevent standard specification | 2 | M | 90
16 | SWR10868 | 0.4 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels,R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Fabrication | Fabrication of work | As per relevent standard specification | 6852 | TO | 2740.8
17 | SWR21241 | 1 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | stringing | stringing of work | As per relevent standard specification | 507 | EA | 507
18 | SMR11915 | 6 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. | Supply | Supply of work | As per relevent standard specification | 2055 | SET | 12330
19 | SMR40011 | 6 | Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . | Supply | Supply of work | As per relevent standard specification | 299 | EA | 1794
20 | SMR22473 | 3 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961)Supply of I-Bolts | Supply | Supply of work | As per relevent standard specification | 294 | EA | 882
21 | SMR40009 | 0.4 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete.Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Supply | Supply of work | As per relevent standard specification | 2181 | TO | 872.4
22 | SWR10877 | 0.4 | Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Supply | Supply of work | As per relevent standard specification | 851 | TO | 340.4
23 | SMR40010 | 0.4 | *)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Supply | Supply of work | As per relevent standard specification | 1293 | TO | 517.2
24 | SWR10879 | 0.4 | (*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Supply | Supply of work | As per relevent standard specification | 482 | TO | 192.8
25 | SWR12331 | 2 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Supply | Supply of work | As per relevent standard specification | 146.63 | EA | 293.26
26 | SWR10881 | 2 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Supply | Supply of work | As per relevent standard specification | 142 | EA | 284
27 | SWR10860 | 5.5 | Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | Supply | Supply of work | As per relevent standard specification | 2113 | M3 | 11621.5
28 | SWR10357 | 7 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Earthing | Earthing Of work | As per relevent standard specification | 1234.2 | EA | 8639.4
29 | SMR40080 | 20 | Cost of Pipes and slabs. Supply of 4" B class GI pipe | Supply | Supply of work | As per relevent standard specification | 800 | M | 16000
30 | SMR11480 | 4 | Supply of earthing pipe with materials.GI eath pipe with 40 mm dia,3mm thcikness with 2.0 M Length | Supply | Supply of work | As per relevent standard specification | 698 | EA | 2792
31 | SMR11485 | 40 | Supply of earthing pipe with materials.GI Flat 25X3 mm | Earthing | Earthing Of work | As per relevent standard specification | 105 | KG | 4200
32 | SWR10522 | 1 | UNLOADING of R.S. Joists 175 x 85 mm | UNLOADING | UNLOADING of work | As per relevent standard specification | 50 | EA | 50
33 | SWR10204 | 1 | LOADING of R.S. Joists 175 x 85 mm | LOADING | LOADING of work | As per relevent standard specification | 76 | EA | 76
34 | SWR10264 | 3 | LOADING of 11 KV,10 KA LAs Station type | LOADING | LOADING of work | As per relevent standard specification | 32 | EA | 96
35 | SWR10582 | 3 | UNLOADING of 11 KV,10 KA LAs Station type | UNLOADING | UNLOADING of work | As per relevent standard specification | 32 | EA | 96
36 | SWR20863 | 2 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation.Erection of 5 Mts RS Joist (Bit) Pole including fixing of Pole Mounted Box | Erection | Erection of work | As per relevent standard specification | 1044.23 | EA | 2088.46
37 | SWR11760 | 1 | Dismantling of Equipment.11KV VCB with Control Pane | Erection | Erection of work | As per relevent standard specification | 2820.28 | EA | 2820.28
38 | SWR20050 | 2 | Dismantling of Equipment.11 KVAB Switch 400/200 A con | Dismantling | Dismantling of work | As per relevent standard specification | 1500 | EA | 3000
39 | SWR10404 | 15 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | Stringing | stringing of work | As per relevent standard specification | 327.68 | M | 4915.2
40 | SWR12125 | 40 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete | Earthing | Earthing Of work | As per relevent standard specification | 14.03 | M | 561.2
41 | SWR10359 | 3 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Earthing | Earthing Of work | As per relevent standard specification | 386 | EA | 1158
42 | SWR10133 | 0.95 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel,iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) | Transport | Transport of work | As per relevent standard specification | 476.34 | TO | 452.523
43 | SWR10397 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc.11 KV LAS station type including earthing | Erection | Erection of work | As per relevent standard specification | 559 | SET | 559
44 | SWR10398 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc.11 KV LAS line type including earthing | Erection | Erection of work | As per relevent standard specification | 505 | SET | 505
45 | SWR10919 | 125 | Fabrication and connecting to risers from earth mat to structures, equipment,marshalling boxes, electrical panels, PLCC panels, fencing posts etc.M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Fabrication | Fabrication of work | As per relevent standard specification | 41 | RMT | 5125
46 | SWR10105 | 2 | Excavation of pits in all soils except hard rock requiring blasting.8.0Mtrs PSCC Poles - 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | Excavation | Excavation of work | As per relevent standard specification | 650 | EA | 1300
Schedule Cost. (Excluding GST) | [8 empty] | 125667.623
|  |  | Schedule Cost. (Excluding GST) | 1881996.313
|  |  | GST@18% | 338759.3363
|  |  | Schedule Cost Total | 2220755.6493