## T-2532-07-05-01-02-003
E-Procurement Schedule (WBS No.T-2532-07-05-01-02-003)
Schedule for Bifurcation of existing 11KV Turkapally agl feeder emanating from 33/11KV Turkapally SS by erection of 1.78KM new 11KV feeder from the same SS which involves laying of 0.48KM 11KV 3X185sq.mm XLPE UG cable (Double Run) and stringing of 1.3KM 11KV SCOH line with 55sq.mm AAA conductor over now proposed and existing poles/Towers along with extension of 11KV bay and erection of 1No. 11KV feeder VCB at 33/11KV Turkapally SS in Aliabad Section of Medchal Sub-Division of Medchal Division and the work executed by Construction Division of Medchal Circle under T&D Improvements to original works (Summer Action Plan works-2026)
Sl.No. | Estimate Quantity (Only figures) | SSR CODES | Item Detailed Specification Description | Item Detailed Specification Description | Item short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
11KV Bay Extension Materials
1 | 3 | SWR10343 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation ERECTION OF LINES-Erection of 9.1M Pole | Electrical Work | Electrical Work | As per relevent standard specification | 2400 | EA | 7200
2 | 1 | SWR10461 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11kv VCB | Electrical Work | Erection Work | As per relevent standard specification | 12000 | EA | 12000
3 | 3 | SWR11039 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) Exca Hard pit w/o blast 0.76X0.76X1.83M | Civil Work | Excavation Work | As per relevent standard specification | 928 | EA | 2784
4 | 2 | SWR10393 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete Erection of 11kv ABSwitch incl earthing | Electrical Work | Erection Work | As per relevent standard specification | 3200 | EA | 6400
5 | 4 | SMR11482 | Supply of CI earth pipe 100 mm dia, 2mt long thickness 10mm with flange as per specication S-CI Pipe earthing 100mm dia 2.75m long | Electrical Work | Supply Work | As per relevent standard specification | 3486 | EA | 13944
6 | 4 | SWR10357 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.6M dia x 0.5 M height . ERECT. OF LINES-Providing of earthing | Electrical Work | Earthing Work | As per relevent standard specification | 1234.2 | EA | 4936.8
7 | 5 | SWR10404 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) Stringing of bus with panther conductor | Electrical Work | Stringing Work | As per relevent standard specification | 327.68 | M | 1638.4
8 | 450 | SWR11879 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) Lay-4C/10C 2.5Sqmm Control Cable | Electrical Work | Laying Work | As per relevent standard specification | 27 | M | 12150
9 | 1 | SWR10869 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. Fabrication of struc.with welding. | Civil Work | Fabrication Work | As per relevent standard specification | 3426 | TO | 3426
10 | 1.32 | SWR10149 | Transport of steel including line materials such as cross arms, clamps, hardware, cable (loose) and other line materials (Including loading and unloading) TRANSPORT OF STEEL MATERIAL 20 TO 30KM | Electrical Work | Transportation Work | As per relevent standard specification | 527.34 | TO | 696.0888
11 | 1 | SWR11862 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Transport of Cond Drum,VCBs >20 & <30Km | Electrical Work | Transportation Work | As per relevent standard specification | 3691.38 | EA | 3691.38
12 | 25.53 | SWR10920 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication. Laying of earth mat,excavation 75x 8mm | Electrical Work | Laying of Work | As per relevent standard specification | 65 | RMT | 1659.45
13 | 2.67 | SWR10356 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Civil Work | Mass Concreting work | As per relevent standard specification | 6579 | M3 | 17565.93
14 | 4 | SWR10359 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | Electrical Work | Erection Work | As per relevent standard specification | 386 | EA | 1544
15 | 3 | SWR12331 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch AB Switch Coil Earthing GI No. 8 Wire | Electrical Work | Electrical Work | As per relevent standard specification | 146.63 | EA | 439.89
16 | 3 | SWR10881 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) Painting AB switch OP rods with PO red | Civil Work | Painting Work | As per relevent standard specification | 142 | EA | 426
17 | 1 | SWR10199 | LOADING AND UN-LOADING of LINE MATERIALS LOADING of 11 KV VCBs&Panel boards | Electrical Work | Loading Work | As per relevent standard specification | 1024 | EA | 1024
18 | 1 | SWR10517 | 11 KV VCBs along with Panel boar UNLOADING of 11 KV VCBs&Panel boards | Electrical Work | Unloading Work | As per relevent standard specification | 1044.48 | EA | 1044.48
19 | 3 | SWR10238 | LOADING of 11 KV AB SWCH Con 200/400 A | Electrical Work | Loading Work | As per relevent standard specification | 80 | EA | 240
20 | 3 | SWR10556 | UNLOADING of 11 KV AB SWCH Con 200/400 A | Electrical Work | Unloading Work | As per relevent standard specification | 80 | EA | 240
21 | 450 | SWR23105 | L-PVC Control Cb 4, 10C | Electrical Work | Loading Work | As per relevent standard specification | 1 | M | 450
22 | 450 | SWR23106 | UL-PVC Control Cb 4, 10C | Electrical Work | Unloading Work | As per relevent standard specification | 0.15 | M | 67.5
23 | 3 | SWR10743 | Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of coping with two coats of white cement (including cost of paint) Painting of supports to a height of 0.3M | Civil Work | Painting Work | As per relevent standard specification | 686 | EA | 2058
24 | 1 | SWR10732 | Con of Plinth for 11kv VCB 1.8x1.8x0.75m | Civil Work | Civil Work | As per relevent standard specification | 27629 | EA | 27629
25 | 3.888 | SWR20768 | Excavation of pits in hard rock requiring blasting. (other than SS) Excavate-Pit in Soil except Hrd Rck | Civil Work | Excavation Work | As per relevent standard specification | 345 | M3 | 1341.36
26 | 1 | SWR20570 | Dismantling of 33KV CT's | Electrical Work | Dismantling Work | As per relevent standard specification | 190 | EA | 190
27 | 1 | SWR10402 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11kv three phase PT s | Electrical Work | Erection Work | As per relevent standard specification | 800 | SET | 800
28 | 1 | SWR11771 | Erection of 24 V Battery along with charger including grouting, giving connections Erect-24V Batery with Chrgr incl grot-SS | Electrical Work | Erection Work | As per relevent standard specification | 1050 | EA | 1050
29 | 1 | SWR11040 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) Ex of Hard pit w/o blast 0.75X0.9X1.95M | Civil Work | Excavation Work | As per relevent standard specification | 990.68 | EA | 990.68
30 | 1 | SWR10346 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erection of RS Joist 175 x 85 mm | Electrical Work | Erection Work | As per relevent standard specification | 1934 | EA | 1934
31 | 1 | SWR10204 | LOADING AND UN-LOADING of LINE MATERIALS LOADING of R.S. Joists 175 x 85 mm | Electrical Work | Loading Work | As per relevent standard specification | 76 | EA | 76
32 | 1 | SWR10522 | UNLOADING of R.S. Joists 175 x 85 mm | Electrical Work | Unloading Work | As per relevent standard specification | 50 | EA | 50
33 | 1 | SWR10640 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables Painting of RS Joist(1C RO, 2C Al.Paint) | Civil Work | Painting Work | As per relevent standard specification | 1132 | EA | 1132
34 | 1 | SWR21277 | Ere 11KV 800A double throw AB Switches | Electrical Work | Erection Work | As per relevent standard specification | 3500 | EA | 3500
134318.9588
11KV line
1 | 18 | SWR10978 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erection of 11 M long PSCC pole | Electrical Work | Erection Work | As per relevent standard specification | 4336.85 | EA | 78063.3
2 | 1.62 | SWR10356 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Civil Work | Civil Work | As per relevent standard specification | 6579 | M3 | 10657.98
3 | 2 | SWR12331 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch AB Switch Coil Earthing GI No. 8 Wire | Electrical Work | Electrical Work | As per relevent standard specification | 146.63 | EA | 293.26
4 | 2 | SWR10881 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) Painting AB switch OP rods with PO red | Civil Work | Painting Work | As per relevent standard specification | 142 | EA | 284
5 | 4 | SWR11230 | 11KV/33KV XLPE UG Cable for all sizes Load-11/33KV XLPE UG Cable for all sizes | Electrical Work | Loading Work | As per relevent standard specification | 1024 | DR | 4096
6 | 4 | SWR11231 | 11KV/33KV XLPE UG Cable for all sizes Unload-11/33KV XLPE UG Cable all sizes | Electrical Work | Unloading Work | As per relevent standard specification | 1024 | DR | 4096
7 | 480 | SWR11982 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Lay-DR 11KV 3x185sqmm UG Cb CC/BT Compsr | Electrical Work | Laying Work | As per relevent standard specification | 1264.64 | M | 607027.2
8 | 2 | SWR10357 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.6M dia x 0.5 M height . ERECT. OF LINES-Providing of earthing | Electrical Work | Earthing Work | As per relevent standard specification | 1234.2 | EA | 2468.4
9 | 30 | SWR12006 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) Raise-DR 11KV 3x185sqmm UG Cb on support | Electrical Work | Raising Cable Work | As per relevent standard specification | 243.53 | M | 7305.9
10 | 100 | SMR40078 | Supply of 150 mm Hume pipe of class NP3 with compresive strength of 35 N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. Supply of 150 mm Hume pipe of class NP3 | Civil Work | Supply Work | As per relevent standard specification | 303 | M | 30300
11 | 24 | SMR40080 | Cost of Pipes and slabs S-4" BClass GI pipe 3.65mm thck 12.2Kg/M | Civil Work | Supply Work | As per relevent standard specification | 800 | M | 19200
12 | 1.3 | SWR10365 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location. Stringing of 55sqmm 33/11kv Line 3 Cond | Electrical Work | Stringing of Work | As per relevent standard specification | 9454.81 | KM | 12291.253
13 | 2 | SWR10393 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete Erection of 11kv ABSwitch incl earthing | Electrical Work | Erection of Work | As per relevent standard specification | 3200 | EA | 6400
14 | 18 | SWR10108 | Excavation of pits in all soils except hard rock requiring blasting EXCAV. OF PIT 0.75 M x 0.9 M x 1.95 M | Civil Work | Excavation of Work | As per relevent standard specification | 730 | EA | 13140
15 | 20 | SWR10356 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Civil Work | Civil Work | As per relevent standard specification | 6579 | M3 | 131580
16 | 1.6 | SWR10149 | Transport of steel including line materials such as cross arms, clamps, hardware, cable (loose) and other line materials (Including loading and unloading) TRANSPORT OF STEEL MATERIAL 20 TO 30KM | Electrical Work | Transportation of Work | As per relevent standard specification | 527.34 | TO | 843.744
17 | 1 | SWR11863 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Transport of Cond Drum,VCBs >30 & <50Km | Electrical Work | Transportation of Work | As per relevent standard specification | 4372.74 | EA | 4372.74
18 | 30 | SMR11487 | Supply of MS bolts & nuts and washers etc of all sizes S-MS Bolts & Nuts,Washers etc., | Electrical Work | Supply of Work | As per relevent standard specification | 91.25 | KG | 2737.5
19 | 1.1 | SWR10869 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. Fabrication of struc.with welding. | Electrical Work | Fabrication of Work | As per relevent standard specification | 3426 | TO | 3768.6
20 | 5 | SWR20308 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | Electrical Work | Transportation of Work | As per relevent standard specification | 407.29 | EA | 2036.45
21 | 10 | SWR34252 | S&R 25x6mm GI Strip for Earthing | Electrical Work | Electrical Work | As per relevent standard specification | 115 | M | 1150
22 | 6 | SWR10653 | Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | Electrical Work | Electrical Work | As per relevent standard specification | 1435.81 | EA | 8614.86
23 | 500 | SWR23200 | Cut-Tree Branch(LT/11/33)&Trnsprt Debris Cut-Tree Branch(LT/11/33)&Trnsprt Debris | Civil Work | Civil Work | As per relevent standard specification | 4 | EA | 2000
24 | 18 | SWR11720 | 1KV side arm 75x40mm Channel 65x65x6mm Angle Fabricate-11KV Side Arm | Electrical Work | Fabrication of Work | As per relevent standard specification | 100 | EA | 1800
25 | 5 | SWR10106 | Excavation of pits in all soils except hard rock requiring blasting EXCAVATION OF PIT 0.6 M x 0.9 M x 1.5 M | Civil Work | Excavation of Work | As per relevent standard specification | 645 | EA | 3225
27 | 5 | SWR11083 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erec of 9.1 Mts PSCC poles for stuts | Electrical Work | Erection of Work | As per relevent standard specification | 2400 | EA | 12000
28 | 2 | SWR10385 | 11 KV 3x185 Sqmm Cable Straight through joint 11kv 3x185 xlpe | Electrical Work | Electrical Work | As per relevent standard specification | 3725.45 | EA | 7450.9
29 | 4 | SWR10390 | Making of Outdoor/Indoor End Termination OD/Idoor end termination 11kv 3x185 xlpe | Electrical Work | Electrical Work | As per relevent standard specification | 2370.63 | EA | 9482.52
30 | 18 | SWR11180 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading) SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | Electrical Work | Electrical Work | As per relevent standard specification | 431.97 | EA | 7775.46
31 | 480 | SWR10988 | Laying of the cable along the footpath through 225mm dia GI pipe for 33KV, 150mm dia GI pipe for 11KV (excluding the cost of GI pipe) Lay-2nd Cable in Excavated Trench | Electrical Work | Laying of Work | As per relevent standard specification | 204.1 | M | 97968
32 | 15 | SMR11485 | Supply of earthing pipe with materials S-Earthing GI flat 25x3 mm incl material | Electrical Work | Supply of Work | As per relevent standard specification | 105 | KG | 1575
| 25 | SWR12125 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete Run-GI Earth Flat 25x3mm from metallic p | Electrical Work | Electrical Work | As per relevent standard specification | 14.03 | M | 350.75
1094354.817
Civil services
1 | 8 | SWR34179 | Hire-JCB to Level & Clear the Site | Civil Work | Civil Work | As per relevent standard specification | 2200 | H | 17600 | 2200
2 | 15.75 | SWR33015 | Excavation in Ordinary Soil | Civil Work | Civil Work | As per relevent standard specification | 513 | M3 | 8079.75 | 513
3 | 22.7 | SWR33041 | CRS Masonary CM(1:6) 2nd Sort | Civil Work | Civil Work | As per relevent standard specification | 5829 | M3 | 132318.3 | 5829
4 | 22.4 | SWR33403 | S&F MS Security Fencing Mesh (2"X2") | Civil Work | Civil Work | As per relevent standard specification | 2310 | M2 | 51744 | 2310
5 | 1 | SWR34446 | S-3/4" dia 30m PVC Braided Hose Pipe | Civil Work | Civil Work | As per relevent standard specification | 1510 | EA | 1510 | 1510
6 | 1 | SMR11594 | S-90W LED fixture set | Civil Work | Civil Work | As per relevent standard specification | 8200 | EA | 8200 | 8200
7 | 50 | SWR33052 | S&Filling with Borrowed Gravel | Civil Work | Civil Work | As per relevent standard specification | 715 | M3 | 35750 | 715
8 | 12.36 | SWR33057 | S&Spreading of 20mm HBG Metal | Civil Work | Civil Work | As per relevent standard specification | 2041 | M3 | 25226.76 | 2041
280428.81
|  |  | Total Schedule Cost |  | 1509102.5858
|  |  | 18% GST |  | 271638.4654
|  |  | Total Cost including GST |  | 1780741.0512