## T-2532-07-05-01-01-001
Schedule(WBS No:WBS NO.T-2532-07-05-01-01-001)
Name of the work: Bifurcation of existing 11KV Bhavanipuram Feeder emanating from 33/11KV Vemana Colony SS by laying of 1.66 KM of 11KV3X185Sq.mm XLPE UG cable (DR) from 33/11KV HMT HILLS SS along with erecting 1No. 11KV Feeder VCB at the same SS in Vemana Colony Section of Miyapur Sub-Division in Kukatpally Division in Medchal Circle under T &D Improvements to original works (Summer Action Plan-2026).
Sl.No. | SSR CODES | Estimate Quantity (Only figures) | Particulars | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item Short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SMR40081 | 30 | Cost of Pipes and slabs.Supply of 6" B class GI pipe | Supply | Supply of work | As per relevent standard specification | 1344 | M | 40320
2 | SWR11982 | 1660 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet,3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, -DR 11KV 3x185sqmm UG Cb CC/BT Compsr | Excavation | Excavation of work | As per relevent standard specification | 1264.64 | M | 2099302.4
3 | SWR12006 | 40 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) -DR 11KV 3x185sqmm UG Cb on support | Erection | Erection of work | As per relevent standard specification | 243.53 | M | 9741.2
4 | SWR10390 | 10 | Making of Outdoor/Indoor End Termination Making 11 KV 3x185 Sqmm Cable Out Door/Indoor end termination | Erection | Erection of work | As per relevent standard specification | 2370.63 | EA | 23706.3
5 | SWR11230 | 10 | Loading of 11/33KV XLPE UG Cable for all sizes | LOADING | LOADING of work | As per relevent standard specification | 1024 | DR | 10240
6 | SWR11231 | 10 | Unloading of 11/33KV XLPE UG Cable all sizes | UNLOADING | UNLOADING of work | As per relevent standard specification | 1024 | DR | 10240
7 | SWR11862 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators,transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Above 20 Km and upto 30 Km with Lorry for each trip | Transport | Transport of work | As per relevent standard specification | 3691.38 | EA | 3691.38
8 | SWR11171 | 10 | Loading of 11/33 KV IN/OUT door kits | LOADING | LOADING of work | As per relevent standard specification | 6 | EA | 60
9 | SWR11152 | 10 | Un-loading of 11/33 KV IN/OUT door kits | UNLOADING | UNLOADING of work | As per relevent standard specification | 4 | EA | 40
10 | SWR11172 | 12 | Loading 11/33KV Straight thr jointkit | LOADING | LOADING of work | As per relevent standard specification | 8 | EA | 96
11 | SWR11153 | 12 | Un-loading 11/33KV Straight thr jointkit | UNLOADING | UNLOADING of work | As per relevent standard specification | 4 | EA | 48
12 | SMR11482 | 5 | Supply of earthing pipe with materials. CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Supply | Supply of work | As per relevent standard specification | 3486 | EA | 17430
13 | SMR11485 | 60 | Supply of earthing pipe with materials.GI flat 25x3 mm incl material | Supply | Supply of work | As per relevent standard specification | 105 | KG | 6300
14 | SWR12125 | 60 | Erection of Equipment.Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LTDistribution box and inter connection of earth pits etc complete | Erection | Erection of work | As per relevent standard specification | 14.03 | M | 841.8
15 | SMR11488 | 50 | Supply of earthing pipe with materials - GI Bolts & Nuts,Washers etc., | Supply | Supply of work | As per relevent standard specification | 117.5 | KG | 5875
16 | SWR10320 | 20 | Fabrication of materials including 2 coats of Red oxide painting. Back clamps with 50 x 6 mm MS Flat | Fabrication | Fabrication of work | As per relevent standard specification | 16 | EA | 320
17 | SMR40078 | 150 | Supply of 150 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993 | Supply | Supply of work | As per relevent standard specification | 303 | M | 45450
18 | SWR10366 | 0.05 | Paving out and stringing of conductor by providing temporary stays, tensioning,sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location. 100 Sqmm Single Circuit (3 Conductors) | Stringing | Stringing of work | As per relevent standard specification | 13856.8 | KM | 692.84
19 | SWR10191 | 1 | LOADING of Conductor drums | LOADING | LOADING of work | As per relevent standard specification | 202 | EA | 202
20 | SWR10509 | 1 | UNLOADING of Conductor drums | UNLOADING | UNLOADING of work | As per relevent standard specification | 100 | EA | 100
21 | SWR10206 | 0.15 | LOADING of MS Channel,Angles,Flats&Rods | LOADING | LOADING of work | As per relevent standard specification | 221 | TO | 33.15
22 | SWR10524 | 0.15 | UNLOADING of MS Channel,Angles,Flats&Rod | UNLOADING | UNLOADING of work | As per relevent standard specification | 185 | TO | 27.75
23 | SWR11248 | 6 | Loading of 11KV Polymer Pin Insulator-GI pin | LOADING | LOADING of work | As per relevent standard specification | 1 | EA | 6
24 | SWR11249 | 6 | Unloading of 11KV Polymer Pin Insulator-GI pin | UNLOADING | UNLOADING of work | As per relevent standard specification | 1 | EA | 6
25 | SWR10301 | 4 | Cutting charges for MS Sections.MS flat of all sizes | Erection | Erection of work | As per relevent standard specification | 2 | EA | 8
26 | SWR10988 | 1660 | Laying of XLPE UG cable Six Run including excavation of trench of size 1050mm wide to 1200mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-2nd Cable in Excavated Trench | Excavation | Excavation of work | As per relevent standard specification | 204.1 | M | 338806
27 | SWR10869 | 0.13 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Fabrication | Fabrication of work | As per relevent standard specification | 3426 | TO | 445.38
28 | SWR10393 | 3 | Erection of AB Switch and aligment complete. 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Erection | Erection of work | As per relevent standard specification | 3200 | EA | 9600
29 | SWR10108 | 4 | Excavation of pits in all soils except hard rock requiring blasting.11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M (1.31 cum) | Excavation | Excavation of work | As per relevent standard specification | 730 | EA | 2920
30 | SWR11266 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation.Box pole 9/10/11 Mtr. | Erection | Erection of work | As per relevent standard specification | 2643.83 | EA | 10575.32
31 | SWR10356 | 4.48 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Erection | Erection of work | As per relevent standard specification | 6579 | M3 | 29473.92
32 | SWR10641 | 4 | Painting of R.S Joist,Box poles including cross arms and clamps with two coat of Al.paint including cost of paint and consumables. | Erection | Erection of work | As per relevent standard specification | 656 | EA | 2624
33 | SWR10357 | 5 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Excavation | Excavation of work | As per relevent standard specification | 1234.2 | EA | 6171
34 | SWR10298 | 4 | Cutting charges for MS Sections.RS Joists 175 x 85 mm | Erection | Erection of work | As per relevent standard specification | 47 | EA | 188
35 | SWR10385 | 12 | UG Cables Joints : Making of Straight through joints 11 KV 3x185 Sqmm Cable | Erection | Erection of work | As per relevent standard specification | 3725.45 | EA | 44705.4
36 | SWR10133 | 2.15 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel,iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) | Transport | Transportation of work | As per relevent standard specification | 476.34 | TO | 1024.13
Schedule Cost. (Excluding GST) | [8 empty] | 2721310.97
|  |  | Schedule Cost. (Excluding GST) | 2721310.97
|  |  | GST@18% | 489835.9746
|  |  | Schedule Cost Total | 3211146.9446