## T-2532-07-05-01-02-002
E-Procurement Schedule (WBS No.T-2532-07-05-01-02-002)
E-Procurement Schedule for providing of 490mtrs of new 11KV feeder from 33/11KV Yellampet SS with laying of 490mtrs of 11KV UG cable along with erection of 1No. 11KV Bay & Breaker for bifurcation existing 11KV Yellampet IDA feeder emanating from 33/11KV Yellampet SS in Medchal Rural Section of Medchal Sub-Division of Medchal Division and the work executed by the Construction Division of Medchal Circle under T&D Improvements to original works under Summer Action Plan-2026
Sl.No. | Estimate Quantity (Only figures) | SSR CODES | Item Detailed Specification Description | Item Detailed Specification Description | Item short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
11KV Bay and VCB
1 | 1 | SWR10461 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11kv VCB | Electrical Work | Erection Work | As per relevent standard specification | 12000 | EA | 12000
2 | 0.88 | SWR10356 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Civil Work | Mass Concreting Work | As per relevent standard specification | 6579 | M3 | 5789.52
3 | 450 | SWR11879 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends Lay-4C/10C 2.5Sqmm Control Cable | Electrical Work | Laying Work | As per relevent standard specification | 27 | M | 12150
4 | 100 | SMR11488 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | Electrical Work | Supply Work | As per relevent standard specification | 117.5 | KG | 11750
5 | 1 | SWR10942 | Wirring, commissioning and testing of Outdoor Sub-station switchgear duly conducting the pre commissioning test as per relevent standards & issue of certificate by CEIG authorised testing EngineerTesting of Outdoor SS switchgear | Electrical Work | Electrical Work | As per relevent standard specification | 1825 | EA | 1825
6 | 1 | SWR10107 | Excavation of pits in all soils except hard rock requiring blasting EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | Excavation | Excavation Work | As per relevent standard specification | 700 | EA | 700
7 | 3 | SWR10238 | Loading of 11KV AB Switch Conventional type LOADING of 11 KV AB SWCH Con 200/400 A | Loading | Loading Work | As per relevent standard specification | 80 | EA | 240
8 | 3 | SMR40025 | Supply of Alluminum PT clamps conforming to A6 of IS 617, with hot dip galvanised bolts and nuts suitable for single zebra / Panther Sup PT clamps for single zebra / Panther | Electrical Work | Supply Work | As per relevent standard specification | 368 | EA | 1104
9 | 1 | SMR40070 | Earth rods with (1) reputed make ISI PVC pipe of 5 feet length, 3 mm thickness, 32 mm dia inside cane wood stick closed both top & bottom ends with caps, (2) reputed make ISI (Finolex/ Polycab/ Havells) first quality flexible PVC wire of 6 Sq.mm multi-strand copper 10 Mtrs length one side crimped with a suitable copper lug, other side fixed with a lug, bolt & nut to a suitable 3 inch long copper heavy duty crocodile clip having insulated sleeves, (3) Copper flat of size 25 mm width 3 mm thick 250 mm length make hook shape fixed to the PVC pipe with 2 No.s 6 mm dia 65 mm length hot dip galvanized bolts triple nuts with a 2 mm thick spring washer and 1 mm thick 4 flat washers and fixing of the copper wire to the bolts with lugs. Supply of Danger boards with clamps | Electrical Work | Earthing Work | As per relevent standard specification | 116 | EA | 116
10 | 12 | SWR10917 | Labour for Fixing of all types of clamps | Electrical Work | Electrical Work | As per relevent standard specification | 65 | EA | 780
11 | 3 | SWR10393 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete Erection of 11kv ABSwitch incl earthing | Electrical Work | Electrical Work | As per relevent standard specification | 3200 | EA | 9600
12 | 1 | SWR11861 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Transport of Cond Drum,VCBs >10 & <20Km | Transportation Work | Transportation Work | As per relevent standard specification | 3299.7 | EA | 3299.7
13 | 1 | SWR10199 | LOADING of 11 KV VCBs&Panel boards | Electrical Work | Loading Work | As per relevent standard specification | 1024 | EA | 1024
14 | 1 | SWR10517 | UNLOADING of 11 KV VCBs&Panel boards | Electrical Work | Un Loading Work | As per relevent standard specification | 1044.48 | EA | 1044.48
15 | 3 | SWR10556 | UNLOADING of 11 KV AB SWCH Con 200/400 A | Electrical Work | Un Loading Work | As per relevent standard specification | 80 | EA | 240
16 | 3 | SMR11482 | S-CI Pipe earthing 100mm dia 2.75m long | Electrical Work | Supply Work | As per relevent standard specification | 3486 | EA | 10458
17 | 0.75 | SWR10206 | LOADING of MS Channel,Angles,Flats&Rods | Electrical Work | Loading Work | As per relevent standard specification | 221 | TO | 165.75
18 | 0.75 | SWR10524 | UNLOADING of MS Channel,Angles,Flats&Rod | Electrical Work | Un Loading Work | As per relevent standard specification | 185 | TO | 138.75
19 | 3 | SWR10265 | LOADING of 11 KV, 10 KA LAs Line type | Electrical Work | Loading Work | As per relevent standard specification | 32 | EA | 96
20 | 3 | SWR10583 | UNLOADING of 11 KV, 10 KA LAs Line type | Electrical Work | Un Loading Work | As per relevent standard specification | 32 | EA | 96
21 | 450 | SWR11701 | Load-PVC Control Cable 10C | Electrical Work | Loading Work | As per relevent standard specification | 1 | M | 450
22 | 450 | SWR11712 | UnLoad-PVC Control Cable 10C | Electrical Work | Un Loading Work | As per relevent standard specification | 1.02 | M | 459
23 | 3 | SWR10359 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | Electrical Work | Providing of RCC Collar Work | As per relevent standard specification | 386 | EA | 1158
24 | 0.5 | SWR10869 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. Fabrication of struc.with welding. | Electrical Work | Electrical Work | As per relevent standard specification | 3426 | TO | 1713
25 | 1 | SWR21241 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) Hoisting post ins&hrd wr 1panther 11kv | Electrical Work | Electrical Work | As per relevent standard specification | 507 | EA | 507
26 | 6 | SMR11915 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. S-Tension HW 3Bolt 1Zebra/Pnthr 150mm | Electrical Work | Electrical Work | As per relevent standard specification | 2055 | SET | 12330
27 | 9 | SMR40011 | Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | Electrical Work | Electrical Work | As per relevent standard specification | 299 | EA | 2691
28 | 3 | SMR22473 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367- 1961) Supply of I-Bolts | Electrical Work | Electrical Work | As per relevent standard specification | 294 | EA | 882
29 | 0.9 | SMR40009 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Sup Material for 1st coat Al. Painting. | Civil Work | Painting of Work | As per relevent standard specification | 2181 | TO | 1962.9
30 | 0.9 | SWR10877 | Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Electrical of Work | Electrical Work | As per relevent standard specification | 851 | TO | 765.9
31 | 0.9 | SMR40010 | Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Electrical Work | Supply Work | As per relevent standard specification | 1293 | TO | 1163.7
32 | 0.9 | SWR10879 | Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Electrical Work | Electrical Work | As per relevent standard specification | 482 | TO | 433.8
33 | 62.5 | SWR10919 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. Earthing for raisers of SS Flat 50x6 mm. | Electrical Work | Fabrication Work | As per relevent standard specification | 41 | RMT | 2562.5
34 | 100 | SWR12510 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) L-Cable Termination to Switchgear | Electrical Work | Cable terminations Work | As per relevent standard specification | 27 | EA | 2700
35 | 3 | SWR12331 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch AB Switch Coil Earthing GI No. 8 Wire | Electrical Work | Making of coil earthing pole Work | As per relevent standard specification | 146.63 | EA | 439.89
36 | 3 | SWR10881 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) Painting AB switch OP rods with PO red | Electrical Work | Painting work | As per relevent standard specification | 142 | EA | 426
37 | 3 | SWR10743 | Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of coping with two coats of white cement (including cost of paint) Painting of supports to a height of 0.3M | Electrical Work | Painting work | As per relevent standard specification | 686 | EA | 2058
38 | 3 | SWR10357 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height ERECT. OF LINES-Providing of earthing | Electrical Work | Earthing Work | As per relevent standard specification | 1234.2 | EA | 3702.6
39 | 10 | SMR11485 | Supply of earthing pipe with materials S-Earthing GI flat 25x3 mm incl material | Electrical Work | Supply Work | As per relevent standard specification | 105 | KG | 1050
40 | 2 | SMR11435 | S-Plain Switches | Electrical Work | Supply Work | As per relevent standard specification | 30 | EA | 60
41 | 2 | SWR11435 | F-Plain switches | Electrical Work | Supply Work | As per relevent standard specification | 13 | EA | 26
42 | 4 | SMR11524 | Supply of Indication LED Lamps 250 V DC (White, blue, Amber) Diameter 22.5 mm suitable for fixing in Control Relay Panels of Circuit Breakers S-Indication LED Lamps(White,Blue,Amber) | Electrical Work | Supply Work | As per relevent standard specification | 130 | EA | 520
43 | 2 | SMR11914 | Supply of Push buttons (with NO contact) self illuminating LED 250 V DC White Diameter 22.5 mm suitable for fixing in Tripping Circuit Healthy Circuit in Control Relay Panels of Circuit Breakers. 220VDC Illuminating Healthy Trip Push Button S-Self Iluminate 220V DC 22.5mm Push Btn | Electrical Work | Supply Work | As per relevent standard specification | 300 | EA | 600
44 | 1 | SWR11380 | Fixing of Hylam Sheet & Cutting of Panel & Fixing of relay | Civil Work | Civil Work | As per relevent standard specification | 2000 | EA | 2000
45 | 3 | SWR12331 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch AB Switch Coil Earthing GI No. 8 Wire | Electrical Work | Making of coil earthing pole Work | As per relevent standard specification | 146.63 | EA | 439.89
46 | 1 | SWR10732 | Con of Plinth for 11kv VCB 1.8x1.8x0.75m | Civil Work | Con of Plinth Work | As per relevent standard specification | 27629 | EA | 27629
47 | 3.888 | SWR20768 | Earth work excavation of in all soils except hard rock requiring blasting. Excavate-Pit in Soil except Hrd Rck | Electrical Work | Excavation Work | As per relevent standard specification | 345 | M3 | 1341.36
48 | 1 | SWR10398 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erect of 11kvLA line type incl earthing | Electrical Work | Erection of AB Switches Work | As per relevent standard specification | 505 | SET | 505
49 | 0.9 | SWR10133 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) TRANSPORT OF STEEL 20 TO 30KM | Electrical Work | Transport of iron materials Work | As per relevent standard specification | 476.34 | TO | 428.706
50 | 20 | SWR10920 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication Laying of earth mat,excavation 75x 8mm | Electrical Work | Laying of earth mat Work | As per relevent standard specification | 65 | RMT | 1300
144922.446
11KV UG cable
1 | 20 | SMR11485 | Supply of earthing pipe with materialsS-Earthing GI flat 25x3 mm incl material | Electrical Work | Supply Work | As per relevent standard specification | 105 | KG | 2100
2 | 20 | SMR11487 | Supply of earthing pipe with materials S-MS Bolts & Nuts,Washers etc., | Electrical Work | Supply Work | As per relevent standard specification | 91.25 | KG | 1825
3 | 2 | SWR11862 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Transport of Cond Drum,VCBs >20 & <30Km | Electrical Work | Transport of conductor drums Work | As per relevent standard specification | 3691.38 | EA | 7382.76
4 | 4 | SWR11230 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Electrical Work | Loading Work | As per relevent standard specification | 1024 | DR | 4096
5 | 4 | SWR11231 | Unload-11/33KV XLPE UG Cable all sizes | Electrical Work | Un Loading Work | As per relevent standard specification | 1024 | DR | 4096
6 | 490 | SWR11982 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Lay-DR 11KV 3x185sqmm UG Cb CC/BT Compsr | Electrical Work | Laying Work | As per relevent standard specification | 1264.64 | M | 619673.6
7 | 4 | SWR10359 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | Electrical Work | Providing of RCC Collar Work | As per relevent standard specification | 386 | EA | 1544
8 | 30 | SWR12006 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe Raise-DR 11KV 3x185sqmm UG Cb on support | Electrical Work | Raising of double run cable Work | As per relevent standard specification | 243.53 | M | 7305.9
9 | 100 | SMR40078 | Supply of 150 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. Supply of 150 mm Hume pipe of class NP3 | Electrical Work | Supply Work | As per relevent standard specification | 303 | M | 30300
10 | 80 | SMR40080 | Cost of Pipes and slabs S-4" BClass GI pipe 3.65mm thck 12.2Kg/M | Civil Work | Supply Work | As per relevent standard specification | 800 | M | 64000
11 | 3 | SWR25089 | S&E-Smart RFID marker | Electrical Work | Electrical Work | As per relevent standard specification | 2745 | EA | 8235
12 | 5 | SMR40085 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 S-RCC Cable Joint/Route Marker | Electrical Work | Supply Work | As per relevent standard specification | 484 | EA | 2420
13 | 2 | SWR10385 | Making of Straight through joints Straight through joint 11kv 3x185 xlpe | Electrical Work | Electrical Work | As per relevent standard specification | 3725.45 | EA | 7450.9
14 | 4 | SWR10390 | Making 11 KV 3x185 Sqmm Cable Out Door/Indoor end termination OD/Idoor end termination 11kv 3x185 xlpe | Electrical Work | Electrical Work | As per relevent standard specification | 2370.63 | EA | 9482.52
15 | 2 | SWR10343 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation ERECTION OF LINES-Erection of 9.1M Pole | Electrical Work | Erection of pole in positionWork | As per relevent standard specification | 2400 | EA | 4800
16 | 2 | SWR10393 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete Erection of 11kv ABSwitch incl earthing | Electrical Work | Erection Work | As per relevent standard specification | 3200 | EA | 6400
17 | 4 | SMR11480 | Supply of GI eath pipe with 40 mm dia,3mm thcikness with 2.0 M Length S-GI pipe earthing 40mm dia 2m long | Electrical Work | Supply Work | As per relevent standard specification | 698 | EA | 2792
18 | 4 | SWR10357 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height ERECT. OF LINES-Providing of earthing | Civil Work | Earthing Work | As per relevent standard specification | 1234.2 | EA | 4936.8
19 | 2 | SWR10107 | 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | Electrical Work | Erection Work | As per relevent standard specification | 700 | EA | 1400
20 | 1.08 | SWR10356 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Civil Work | Mass concreting of supports Work | As per relevent standard specification | 6579 | M3 | 7105.32
21 | 490 | SWR10988 | Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) Lay-2nd Cable in Excavated Trench | Electrical Work | Laying Work | As per relevent standard specification | 204.1 | M | 100009
22 | [8 empty] | 897354.8
Civil services
1 | 8 | SWR34179 | Hire-JCB to Level & Clear the Site | Civil Work | Civil Work | As per relevent standard specification | 2200 | H | 17600
2 | 15.75 | SWR33015 | Excavation in Ordinary Soil | Civil Work | Civil Work | As per relevent standard specification | 513 | M3 | 8079.75
3 | 22.7 | SWR33041 | CRS Masonary CM(1:6) 2nd Sort | Civil Work | Civil Work | As per relevent standard specification | 5829 | M3 | 132318.3
4 | 22.4 | SWR33403 | S&F MS Security Fencing Mesh (2"X2") | Civil Work | Civil Work | As per relevent standard specification | 2310 | M2 | 51744
5 | 1 | SWR34446 | S-3/4" dia 30m PVC Braided Hose Pipe | Civil Work | Civil Work | As per relevent standard specification | 1510 | EA | 1510
6 | 1 | SMR11594 | S-90W LED fixture set | Civil Work | Civil Work | As per relevent standard specification | 8200 | EA | 8200
7 | 50 | SWR33052 | S&Filling with Borrowed Gravel | Civil Work | Civil Work | As per relevent standard specification | 715 | M3 | 35750
8 | 12.36 | SWR33057 | S&Spreading of 20mm HBG Metal | Civil Work | Civil Work | As per relevent standard specification | 2041 | M3 | 25226.76
280428.81
|  |  | Total Schedule Cost |  | 1322706.056
|  |  | GST (18%) |  | 238087.0901
|  |  | Total Schedule Cost (Including GST) |  | 1560793.1461