## T-2532-07-05-01-02-004
E- Procurment Schedule (WBS No.T-2532-07-05-01-02-004)
E- Procurment Schedule for bifurcation of the existing 11KV Doolapally feeder emanating from 33/11 KV Doolapally SS by erection of new 11KV feeder from the same SS which involves laying of 0.99KM 11KV 3X185sq.mm XLPE UG cable (Double Run) along with bay extension & erection of 1No. 11KV feeder VCB at 33/11 KV Doolapally SS in Kompally Section of Quthbullapur Sub-Division in Medchal Division and the work executed by the Construction Division of Medchal Circle under T&D Improvements to original works (Summer Action Plan-2026).
11KV BAy AND VCB
Sl.No. | SSR CODES | Estimate Quantity (Only figures) | Particulars | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item Short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SWR10461 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11kv VCB | Electrical work | Erection work | As per relevent standard specification | 12000 | EA | 12000
2 | SMR11482 | 4 | Supply of earthing pipe with materials S-CI Pipe earthing 100mm dia 2.75m long | Electrical work | Supply work | As per relevent standard specification | 3486 | EA | 13944
3 | SWR10356 | 3.24 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Civil work | Mass concreting of supports work | As per relevent standard specification | 6579 | M3 | 21315.96
4 | SWR11879 | 600 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . Lay-4C/10C 2.5Sqmm Control Cable | Electrical work | Laying work | As per relevent standard specification | 27 | M | 16200
5 | SMR11488 | 50 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | Electrical work | Supply work | As per relevent standard specification | 117.5 | KG | 5875
6 | SWR10942 | 1 | Wirring, commissioning and testing of Outdoor Sub-station switchgear duly conducting the pre commissioning test as per relevent standards & issue of certificate by CEIG authorised testing Engineer Testing of Outdoor SS switchgear | Electrical work | Electrical work | As per relevent standard specification | 1825 | EA | 1825
7 | SWR11039 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders Exca Hard pit w/o blast 0.76X0.76X1.83M | Civil work | Excavation work | As per relevent standard specification | 928 | EA | 3712
8 | SWR10238 | 3 | Loading of 11KV AB Switch Conventional type LOADING of 11 KV AB SWCH Con 200/400 A | Electrical work | Loading of work | As per relevent standard specification | 80 | EA | 240
9 | SMR40025 | 6 | Supply of Alluminum PT clamps conforming to A6 of IS 617, with hot dip galvanised bolts and nuts suitable for single zebra / Panther Sup PT clamps for single zebra / Panther | Electrical work | Supply work | As per relevent standard specification | 368 | EA | 2208
10 | SMR40070 | 1 | Earth rods with (1) reputed make ISI PVC pipe of 5 feet length, 3 mm thickness, 32 mm dia inside cane wood stick closed both top & bottom ends with caps, (2) reputed make ISI (Finolex/ Polycab/ Havells) first quality flexible PVC wire of 6 Sq.mm multi-strand copper 10 Mtrs length one side crimped with a suitable copper lug, other side fixed with a lug, bolt & nut to a suitable 3 inch long copper heavy duty crocodile clip having insulated sleeves, (3) Copper flat of size 25 mm width 3 mm thick 250 mm length make hook shape fixed to the PVC pipe with 2 No.s 6 mm dia 65 mm length hot dip galvanized bolts triple nuts with a 2 mm thick spring washer and 1 mm thick 4 flat washers and fixing of the copper wire to the bolts with lugs.Supply of Danger boards with clamps | Electrical work | Earthing work | As per relevent standard specification | 116 | EA | 116
11 | SWR10917 | 15 | Labour for Fixing of all types of clamps Labour for Fixing of all types of clamps | Electrical work | Electrical work | As per relevent standard specification | 65 | EA | 975
12 | SWR10393 | 3 | Erection of AB Switch and aligment complete Erection of 11kv ABSwitch incl earthing | Elecrical work | Erection work | As per relevent standard specification | 3200 | EA | 9600
13 | SWR11861 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Transport of Cond Drum,VCBs >10 & <20Km | Electrical work | Transportation of work | As per relevent standard specification | 3299.7 | EA | 3299.7
14 | SWR10199 | 1 | Loading of 11 KV VCBs along with Panel boards LOADING of 11 KV VCBs&Panel boards | Electrical work | LOADING of work | As per relevent standard specification | 1024 | EA | 1024
15 | SWR10517 | 1 | Un loading of 11 KV VCBs along with Panel boards UNLOADING of 11 KV VCBs&Panel boards | Electrical work | UNLOADING of work | As per relevent standard specification | 1044.48 | EA | 1044.48
16 | SWR10556 | 3 | UNLOADING of 11 KV AB SWCH Con 200/400 A | Electrical work | UNLOADING of work | As per relevent standard specification | 80 | EA | 240
17 | SWR20863 | 2 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation R.S. joist box poles erection complete | Electrical work | Erection work | As per relevent standard specification | 1044.23 | EA | 2088.46
18 | SMR11482 | 4 | Supply of earthing pipe with materials S-CI Pipe earthing 100mm dia 2.75m long | Electrical work | Supply work | As per relevent standard specification | 3486 | EA | 13944
19 | SWR10204 | 1 | LOADING of R.S. Joists 175 x 85 mm | Electrical work | LOADING work | As per relevent standard specification | 76 | EA | 76
20 | SWR10522 | 1 | UNLOADING of R.S. Joists 175 x 85 mm | Electrical work | UNLOADING work | As per relevent standard specification | 50 | EA | 50
21 | SWR10206 | 1.4 | LOADING of MS Channel,Angles,Flats&Rods | Electrical work | LOADING work | As per relevent standard specification | 221 | TO | 309.4
22 | SWR10524 | 1.4 | UNLOADING of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING work | As per relevent standard specification | 185 | TO | 259
23 | SWR10265 | 3 | LOADING of 11 KV, 10 KA LAs Line type | Electrical work | LOADING work | As per relevent standard specification | 32 | EA | 96
24 | SWR10583 | 3 | UNLOADING of 11 KV, 10 KA LAs Line type | Electrical work | UNLOADING work | As per relevent standard specification | 32 | EA | 96
25 | SWR11701 | 600 | Load-PVC Control Cable 10C | Electrical work | LOADING work | As per relevent standard specification | 1 | M | 600
26 | SWR11712 | 600 | UnLoad-PVC Control Cable 10C | Electrical work | UNLOADING work | As per relevent standard specification | 1.02 | M | 612
27 | SWR10298 | 4 | Cutting charges for MS Sections Cutting Charges for RS joist 175x85mm | Electrical work | Electrical work | As per relevent standard specification | 47 | EA | 188
28 | SWR10359 | 4 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | Electrical work | Erection fwork | As per relevent standard specification | 386 | EA | 1544
29 | SWR10868 | 1 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection Fabrication of struc.with power drilling | Electrical work | Fabrication work | As per relevent standard specification | 6852 | TO | 6852
30 | SWR21241 | 1 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) Hoisting post ins&hrd wr 1panther 11kv | Electrical work | Electrical work | As per relevent standard specification | 507 | EA | 507
31 | SMR11915 | 6 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. S-Tension HW 3Bolt 1Zebra/Pnthr 150mm | Electrical work | Electrical work | As per relevent standard specification | 2055 | SET | 12330
32 | SWR11890 | 0.062 | Coping & Muffing-Iron Pole Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt | Civil work | Civil work | As per relevent standard specification | 3893.06 | M3 | 241.3697
33 | SMR40011 | 9 | Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | Electrical Work | Supply Work | As per relevent standard specification | 299 | EA | 2691
34 | SMR22473 | 6 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367- 1961) Supply of I-Bolts | Electrical work | Supply work | As per relevent standard specification | 294 | EA | 1764
35 | SMR40009 | 1.65 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Sup Material for 1st coat Al. Painting. | Electrical work | Painting of work | As per relevent standard specification | 2181 | TO | 3598.65
36 | SWR10877 | 1.65 | Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Electrical work | Electrical work | As per relevent standard specification | 851 | TO | 1404.15
37 | SMR40010 | 1.65 | Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Electrical work | Painting work | As per relevent standard specification | 1293 | TO | 2133.45
38 | SWR10879 | 1.65 | Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium Labour for 2nd coat Al. Painting. | Electrical work | Electrical work | As per relevent standard specification | 482 | TO | 795.3
39 | SWR10920 | 21.27 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication Laying of earth mat,excavation 75x 8mm | Electrical work | Laying of work | As per relevent standard specification | 65 | RMT | 1382.55
40 | SWR10919 | 125 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. Earthing for raisers of SS Flat 50x6 mm. | Electrical work | Fabrication of work | As per relevent standard specification | 41 | RMT | 5125
41 | SWR12510 | 100 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) L-Cable Termination to Switchgear | Electrical work | Electrical of work | As per relevent standard specification | 27 | EA | 2700
42 | SWR12331 | 3 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch AB Switch Coil Earthing GI No. 8 Wire | Civil work | Painting work | As per relevent standard specification | 146.63 | EA | 439.89
43 | SWR10881 | 3 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) Painting AB switch OP rods with PO red | Civil work | Painting work | As per relevent standard specification | 142 | EA | 426
44 | SWR10743 | 3 | Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of coping with two coats of white cement (including cost of paint) Painting of supports to a height of 0.3M | Electrical work | Painting work | As per relevent standard specification | 686 | EA | 2058
45 | SMR11485 | 10 | Supply of earthing pipe with materials S-Earthing GI flat 25x3 mm incl material | Civil work | Civil of work | As per relevent standard specification | 105 | KG | 1050
46 | SMR11435 | 2 | S-Plain Switches | Supply work | Supply of work | As per relevent standard specification | 30 | EA | 60
47 | SWR11435 | 2 | F-Plain switches | Earthing work | Earthing of work | As per relevent standard specification | 13 | EA | 26
48 | SMR11524 | 4 | S-Indication LED Lamps(White,Blue,Amber) | Supply work | Supply of work | As per relevent standard specification | 130 | EA | 520
49 | SMR11914 | 2 | S-Self Iluminate 220V DC 22.5mm Push Btn | Supply work | Supply of work | As per relevent standard specification | 300 | EA | 600
50 | SWR11380 | 1 | Fix-Hylam sheet-Cutting of Panel | Civil work | Civil of work | As per relevent standard specification | 2000 | EA | 2000
51 | SWR10732 | 1 | Con of Plinth for 11kv VCB 1.8x1.8x0.75m | Civil work | Civil work | As per relevent standard specification | 27629 | EA | 27629
52 | SWR20768 | 3.888 | Earth work excavation of in all soils except hard rock requiring blasting. Excavate-Pit in Soil except Hrd Rck |  |  | As per relevent standard specification | 345 | M3 | 1341.36
53 | SWR10343 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation ERECTION OF LINES-Erection of 9.1M Pole | Electrical work | Erection work | As per relevent standard specification | 2400 | EA | 9600
54 | SWR20308 | 4 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading) SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | Electrical work | Transportation work | As per relevent standard specification | 407.29 | EA | 1629.16
55 | SWR11230 | 1 | Load-11/33KV XLPE UG Cable for all sizes | Electrical work | Loading work | As per relevent standard specification | 1024 | DR | 1024
56 | SWR11231 | 1 | Unload-11/33KV XLPE UG Cable all sizes | Electrical work | Unloading work | As per relevent standard specification | 1024 | DR | 1024
57 | SWR11981 | 70 | Lay-DR 11KV 3x300sqmm UG Cb CC/BT Compsr | Electrical work | Laying work | As per relevent standard specification | 1264.64 | M | 88524.8
58 | SWR12005 | 30 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) Raise-DR 11KV 3x300sqmm UG Cb on support | Electrical work | Raising of double run cable work | As per relevent standard specification | 275.4 | M | 8262
59 | SMR40080 | 20 | Cost of Pipes and slabs S-4" BClass GI pipe 3.65mm thck 12.2Kg/M | Electrical work | Supply work | As per relevent standard specification | 800 | M | 16000
60 | SWR10391 | 4 | Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination OD/Idoor end termination 11kv 3x300 xlpe | Electrical work | Electrical work | As per relevent standard specification | 2370.63 | EA | 9482.52
61 | SWR10988 | 70 | Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) Lay-2nd Cable in Excavated Trench | Electrical work | Laying work | As per relevent standard specification | 204.1 | M | 14287
62 | SWR10357 | 4 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height ERECT. OF LINES-Providing of earthing | Electrical work | Earthing work | As per relevent standard specification | 1234.2 | EA | 4936.8
63 | SWR10398 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erect of 11kvLA line type incl earthing | Electrical work | Erection work | As per relevent standard specification | 505 | SET | 505
64 | SWR10105 | 2 | Excavation of pits in all soils except hard rock requiring blasting EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | Electrical work | Excavation work | As per relevent standard specification | 650 | EA | 1300
Schedule Cost. (Excluding GST) | [8 empty] | 347731.9997
11KV UG cable
1 | SMR11487 | 50 | S-MS Bolts & Nuts,Washers etc., | Electrical work | Supply work | As per relevent standard specification | 91.25 | KG | 4562.5
2 | SWR11862 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Transport of Cond Drum,VCBs >20 & <30Km | Electrical work | Transportationn work | As per relevent standard specification | 3691.38 | EA | 7382.76
3 | SWR11230 | 4 | Loading of 11KV/33KV XLPE UG Cable for all sizes Load-11/33KV XLPE UG Cable for all sizes | Electrical work | Loading work | As per relevent standard specification | 1024 | DR | 4096
4 | SWR11231 | 4 | Un loading of 11KV/33KV XLPE UG Cable for all sizes Unload-11/33KV XLPE UG Cable all sizes | Electrical work | Unloading work | As per relevent standard specification | 1024 | DR | 4096
5 | SWR11982 | 900 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts Lay-DR 11KV 3x185sqmm UG Cb CC/BT Compsr | Electrical work | Laying work | As per relevent standard specification | 1264.64 | M | 1138176
6 | SWR10359 | 4 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | Electrical work | Providing of RCC Collar work | As per relevent standard specification | 386 | EA | 1544
7 | SWR12006 | 30 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) Raise-DR 11KV 3x185sqmm UG Cb on support | Electrical work | Raising of double run cable work | As per relevent standard specification | 243.53 | M | 7305.9
8 | SMR40078 | 100 | Supply of 150 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. Supply of 150 mm Hume pipe of class NP3 | Electrical work | Supply work | As per relevent standard specification | 303 | M | 30300
9 | SMR40080 | 24 | Cost of Pipes and slabs S-4" BClass GI pipe 3.65mm thck 12.2Kg/M | Civil of work | Civil of work | As per relevent standard specification | 800 | M | 19200
10 | SWR11990 | 90 | Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) Lay-DR 11KV 3x185sqmm UG Cb CC/BT RdCrsg | Electrical work | Laying work | As per relevent standard specification | 1449.06 | M | 130415.4
11 | SWR25089 | 3 | S&E-Smart RFID marker | Electrical work | Erection work | As per relevent standard specification | 2745 | EA | 8235
12 | SMR40085 | 5 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 S-RCC Cable Joint/Route Marker | Electrical work | Electrical work | As per relevent standard specification | 484 | EA | 2420
13 | SWR10393 | 2 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete Erection of 11kv ABSwitch incl earthing | Electrical work | Erection work | As per relevent standard specification | 3200 | EA | 6400
14 | SMR11480 | 4 | Supply of GI eath pipe with 40 mm dia,3mm thcikness with 2.0 M Length S-GI pipe earthing 40mm dia 2m long | Electrical work | Electrical work | As per relevent standard specification | 698 | EA | 2792
15 | SWR10357 | 4 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height ERECT. OF LINES-Providing of earthing | Electrical work | Erection work | As per relevent standard specification | 1234.2 | EA | 4936.8
16 | SWR10343 | 2 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation ERECTION OF LINES-Erection of 9.1M Pole | Electrical work | Erection work | As per relevent standard specification | 2400 | EA | 4800
17 | SWR10107 | 2 | Excavation of pits in all soils except hard rock requiring blasting EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | Electrical work | Excavation work | As per relevent standard specification | 700 | EA | 1400
18 | SWR10356 | 1.08 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Civil work | Mass concreting of supports work | As per relevent standard specification | 6579 | M3 | 7105.32
19 | SWR10391 | 4 | Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination OD/Idoor end termination 11kv 3x300 xlpe | Electrical work | Electrical work | As per relevent standard specification | 2370.63 | EA | 9482.52
20 | SWR10386 | 4 | Making of Straight through joints Straight through joint 11kv 3x300 xlpe | Electrical work | Supply work | As per relevent standard specification | 3725.45 | EA | 14901.8
21 | SMR11483 | 2 | Supply of earthing pipe with materials S-CI Pipe earthing 80mm dia 2.75m long | Electrical work | Supply work | As per relevent standard specification | 2789 | EA | 5578
22 | SWR10357 | 2 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M heigh ERECT. OF LINES-Providing of earthing | Electrical work | UNLOADING of work | As per relevent standard specification | 1234.2 | EA | 2468.4
23 | SWR10988 | 990 | Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) Lay-2nd Cable in Excavated Trench | Electrical work | LOADING of work | As per relevent standard specification | 204.1 | M | 202059
Schedule Cost. (Excluding GST) | [8 empty] | 1619657.4
civil works
1 | SWR34179 | 8 | Hire-JCB to Level & Clear the Site | Civil work | Civil work | As per relevent standard specification | 2200 | H | 17600
2 | SWR33015 | 15.75 | Excavation in Ordinary Soil | Civil work | Civil work | As per relevent standard specification | 513 | M3 | 8079.75
3 | SWR33041 | 22.7 | CRS Masonary CM(1:6) 2nd Sort | Civil work | Civil work | As per relevent standard specification | 5829 | M3 | 132318.3
4 | SWR33403 | 22.4 | S&F MS Security Fencing Mesh (2"X2") | Civil work | Civil work | As per relevent standard specification | 2310 | M2 | 51744
5 | SWR34446 | 1 | S-3/4" dia 30m PVC Braided Hose Pipe | Civil work | Civil work | As per relevent standard specification | 1510 | EA | 1510
6 | SMR11594 | 1 | S-90W LED fixture set | Civil work | Civil work | As per relevent standard specification | 8200 | EA | 8200
| SWR33052 | 50 | S&Filling with Borrowed Gravel | Civil work | Civil work | As per relevent standard specification | 715 | M3 | 35750
7 | SWR33057 | 12.36 | S&Spreading of 20mm HBG Metal | Civil work | Civil work | As per relevent standard specification | 2041 | M3 | 25226.76
Schedule Cost. (Excluding GST) | [8 empty] | 280428.81
|  |  | TOTAL Schedule Cost. (Excluding GST) | 2247818.2097
|  |  | GST@18% | 404607.2777
|  |  | TOTAL Schedule Cost | 2652425.4875