## E-Pro Schedule
SCHEDULE
Name of the Work:- Providing of 33KV alternate source to 33/11KV Chengicherla SS from 33KV OU Lalaguda feeder which involves laying of 0.68KM 33KV XLPE 3X400sq.mm UG cable (Double Run) from Chengicherla main road to Chengicherla SS in Ghatkesar Sub-Division of Keesara Division in Habsiguda Circle under T&D Improvements to original works (Summer Action Plan-2025-26) (WBS : T-2531-14-06-01-02-003)
Sl.No | Estimate Quantity (Only figures) | SAP Code | Item Detailed Specification Description | Work Type eg.Earth Work, Electrical works..etc., (Upto 200 Characters) | Item short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
33KV Line:
1 | 680 | SWR11980 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV- In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil/CC | Electrical work | Lay-DR 33KV 3x400sqmm UG Cb CC/BT Compsr | As per relevent standard specification | 1388.84 | M | 944411.2
2 | 20 | SWR12004 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Electrical work | Raise-DR 33KV 3x400sqmm UG Cb on support | As per relevent standard specification | 323.85 | M | 6477
3 | 680 | SWR10988 | Laying of XLPE UG cable Six Run including excavation of trench of size 1050mm wide to 1200mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and to 1200mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) | Electrical work | Lay-2nd Cable in Excavated Trench | As per relevent standard specification | 204.1 | M | 138788
4 | 4 | SWR10387 | Making of Outdoor/Indoor End Termination | Electrical work | OD/Idoor end termination 33kv 3x400 xlpe | As per relevent standard specification | 2764.76 | EA | 11059.04
5 | 5 | SWR10382 | Making of Straight through joints | Electrical work | Straight through joint 33kv 3x400 xlpe | As per relevent standard specification | 5700.78 | EA | 28503.9
6 | 2 | SWR10109 | Excavation of pits in all soils except hard rock requiring blasting | Civil Work | EXCAVATION OF PIT(3.0" x 3.0" x 7.6") | As per relevent standard specification | 842.78 | EA | 1685.56
7 | 2 | SWR10642 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable, Painting of RS Joist on inner phasing with red Oxide before Joining as box pole. | Civil Work | Fabricate&Paint-175x85/150x75mm RS Joist | As per relevent standard specification | 512.55 | EA | 1025.1
8 | 2 | SWR11267 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation, for RS Joist, Rail poles Supply & Fabrication of bottom plate with 6mm thichness and for Box poles Supply & Fabrication of Top & Bottom plate with 6mm thichness | Electrical work | Erect-12Meter Box pole | As per relevent standard specification | 3901.37 | EA | 7802.74
9 | 2 | SWR10640 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Civil Work | Painting of RS Joist(1C RO, 2C Al.Paint) | As per relevent standard specification | 1132 | EA | 2264
10 | 2.1 | SWR10356 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Civil Work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 13815.9
11 | 0.06 | SWR11890 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Civil Work | Coping & Muffing-Iron Pole | As per relevent standard specification | 3893 | M3 | 233.58
12 | 12 | SMR12227 | Supply of 33kV cable support cable clamps& nuts | Supply of Material | S-33KV Cb Support Cb Clamps & Nuts | As per relevent standard specification | 500 | EA | 6000
13 | 6 | SMR11483 | Supply of CI eath pipe with 80mm dia,2.0 M Length | Supply of Material | S-CI Pipe earthing 80mm dia 2.75m long | As per relevent standard specification | 2789 | EA | 16734
14 | 6 | SWR10357 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Electrical work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 7405.2
15 | 6 | SWR10359 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Civil Work | ERECT. OF LINES-Providing of RCC collar | As per relevent standard specification | 386 | EA | 2316
16 | 36 | SMR11485 | Supply of GI Flat 25X3 mm | Supply of Material | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 3780
17 | 60 | SWR12125 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete | Electrical work | Run-GI Earth Flat 25x3mm from metallic p | As per relevent standard specification | 14.03 | M | 841.8
18 | 350 | SMR40082 | Supply of 9" B class GI pipe | Supply of Material | S-9" B Class GI pipe 7.3mm thck 28.8Kg/M | As per relevent standard specification | 1113 | M | 389550
19 | 3 | SWR11862 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, Battery Chargers with Batteries, RMU, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Above 20 Km and upto 30 Km with Lorry for each trip | Civil Work | Transport of Cond Drum,VCBs >20 & <30Km | As per relevent standard specification | 3691.38 | EA | 11074.14
20 | 4 | SWR11230 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Civil Work | Load-11/33KV XLPE UG Cable for all sizes | As per relevent standard specification | 1024 | DR | 4096
21 | 4 | SWR11231 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Civil Work | Unload-11/33KV XLPE UG Cable all sizes | As per relevent standard specification | 1024 | DR | 4096
22 | 4 | SWR11171 | Loading of 33/11KV XLPE UG Cable End Termination Kits for all sizes | Civil Work | Loading of 11/33 KV IN/OUT door kits | As per relevent standard specification | 6 | EA | 24
23 | 4 | SWR11152 | Un loading of 33/11KV XLPE UG Cable End Termination Kits for all sizes | Civil Work | Un-loading of 11/33 KV IN/OUT door kits | As per relevent standard specification | 4 | EA | 16
24 | 5 | SWR11172 | Loading of 33/KV XLPE UG CableStraight Through Joint Kits for all sizes | Civil Work | Loading 11/33KV Straight thr jointkit | As per relevent standard specification | 8 | EA | 40
25 | 5 | SWR11153 | Un loading of 33/KV XLPE UG CableStraight Through Joint Kits for all sizes | Civil Work | Un-loading 11/33KV Straight thr jointkit | As per relevent standard specification | 4 | EA | 20
26 | 2 | SWR10392 | Erection of 33 KV AB Switch including alignment and earthing | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 9000
27 | 2 | SWR10881 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Civil Work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 284
28 | 2 | SWR12331 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Electrical work | AB Switch Coil Earthing GI No. 8 Wire | As per relevent standard specification | 146.63 | EA | 293.26
29 | 10 | SMR11486 | Supply of GI wire No 8 | Supply of Material | S-Earthing GI Wire No 8 incl mat | As per relevent standard specification | 105 | KG | 1050
33KV Bay Extension:
30 | 4 | SWR10107 | Excavation of pits in all soils except hard rock requiring blasting 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | Civil Work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 2800
31 | 4 | SWR10343 | Erection of 9.1Meter PSCC pole in position, aligning and setting to work, fixing of cross arms and top clamps, clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 9600
32 | 2.16 | SWR10356 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Civil Work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 14210.64
33 | 1.1 | SWR10869 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | Civil Work | Fabrication of struc.with welding. | As per relevent standard specification | 3426 | TO | 3768.6
34 | 1 | SWR10460 | Erection of 33 KV VCB with Control Panel | Electrical work | Erection of 33kv VCB | As per relevent standard specification | 12500 | EA | 12500
35 | 3 | SWR10392 | Erection of 33 KV AB Switch including alignment and earthing | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 13500
36 | 3 | SWR10881 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) office red colour (including cost of paint) | Civil Work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 426
37 | 3 | SWR12331 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Electrical work | AB Switch Coil Earthing GI No. 8 Wire | As per relevent standard specification | 146.63 | EA | 439.89
38 | 300 | SWR11879 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends | Electrical work | Lay-4C/10C 2.5Sqmm Control Cable | As per relevent standard specification | 27 | M | 8100
39 | 1 | SWR10942 | Wirring, commissioning and testing of Outdoor Sub-station switchgear duly conducting the pre commissioning test as per relevent standards & issue of certificate by CEIG authorised testing Engineer | Electrical work | Testing of Outdoor SS switchgear | As per relevent standard specification | 1825 | EA | 1825
40 | 6 | SMR11482 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Supply of Material | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 20916
41 | 6 | SWR10357 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Electrical work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 7405.2
42 | 6 | SWR10359 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Civil Work | ERECT. OF LINES-Providing of RCC collar | As per relevent standard specification | 386 | EA | 2316
43 | 43 | SWR10920 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication 75x 8mm MS Flat / GI Flat | Electrical work | Laying of earth mat,excavation 75x 8mm | As per relevent standard specification | 65 | RMT | 2795
44 | 85 | SWR10919 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc.M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Civil Work | Earthing for raisers of SS Flat 50x6 mm. | As per relevent standard specification | 41 | RMT | 3485
45 | 18 | SMR40011 | Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating | Supply of Material | Sup T clamp LM6 Al alloy of 12 mm, 800 A | As per relevent standard specification | 299 | EA | 5382
46 | 6 | SMR11915 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | Supply of Material | S-Tension HW 3Bolt 1Zebra/Pnthr 150mm | As per relevent standard specification | 2055 | SET | 12330
47 | 21 | SWR10917 | Labour for Fixing of all types of clamps | Civil Work | Labour for Fixing of all types of clamps | As per relevent standard specification | 65 | EA | 1365
48 | 1 | SWR10198 | Loading of 33 KV VCBs along with Panel boards | Civil Work | LOADING of 33 KV VCBs&Panel boards | As per relevent standard specification | 1024 | EA | 1024
49 | 1 | SWR10516 | Un loading of 33 KV VCBs along with Panel boards | Civil Work | UNLOADING of 33 KV VCBs&Panel boards | As per relevent standard specification | 1044.48 | EA | 1044.48
50 | 3 | SWR10239 | Loading of 33KV 800 Amps AB Switch | Civil Work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 378
51 | 3 | SWR10557 | Un loading of 33KV 800 Amps AB Switch | Civil Work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 237
52 | 1.5 | SWR10206 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Civil Work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 331.5
53 | 1.5 | SWR10524 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Civil Work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 277.5
54 | 1.5 | SWR10133 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) | Civil Work | TRANSPORT OF STEEL 20 TO 30KM | As per relevent standard specification | 476.34 | TO | 714.51
55 | 1 | SWR11862 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, Battery Chargers with Batteries, RMU, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Above 20 Km and upto 30 Km with Lorry for each trip | Civil Work | Transport of Cond Drum,VCBs >20 & <30Km | As per relevent standard specification | 3691.38 | EA | 3691.38
56 | 1.5 | SMR40009 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc | Civil Work | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 3271.5
57 | 1.5 | SWR10877 | Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Civil Work | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 1276.5
58 | 1.5 | SMR40010 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Civil Work | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 1939.5
59 | 1.5 | SWR10879 | Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium | Civil Work | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 723
60 | 3 | SWR10963 | Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium | Civil Work | Painting of Name Plates for any equipmen | As per relevent standard specification | 122 | EA | 366
61 | 2 | SWR10396 | Erection of 33 KV LAS station/Line type including earthing | Electrical work | Erect of 33kv LA stn type incl earthing | As per relevent standard specification | 880 | SET | 1760
62 | 6 | SWR20685 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | Civil Work | Cement concrete with 40MM metal VCB plin | As per relevent standard specification | 5160 | M3 | 30960
63 | 4.8 | SWR23224 | Excavate-Pit for 33KV VCB | Civil Work | Excavate-Pit for 33KV VCB | As per relevent standard specification | 331 | M3 | 1588.8
64 | 5 | SWR10404 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | Electrical work | Stringing of bus with panther conductor | As per relevent standard specification | 327.68 | M | 1638.4
65 | 100 | SWR11980 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV- In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil/CC | Electrical work | Lay-DR 33KV 3x400sqmm UG Cb CC/BT Compsr | As per relevent standard specification | 1388.84 | M | 138884
66 | 25 | SWR12004 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Electrical work | Raise-DR 33KV 3x400sqmm UG Cb on support | As per relevent standard specification | 323.85 | M | 8096.25
67 | 100 | SWR10988 | Laying of 2nd Cable in Excavated Trench | Electrical work | Lay-2nd Cable in Excavated Trench | As per relevent standard specification | 204.1 | M | 20410
68 | 4 | SWR10387 | Making of Outdoor/Indoor End Termination | Electrical work | OD/Idoor end termination 33kv 3x400 xlpe | As per relevent standard specification | 2764.76 | EA | 11059.04
69 | 50 | SMR40082 | Supply of 9" B class GI pipe | Supply of Material | S-9" B Class GI pipe 7.3mm thck 28.8Kg/M | As per relevent standard specification | 1113 | M | 55650
70 | 12 | SMR12227 | Supply of 33kV cable support cable clamps& nuts | Supply of Material | S-33KV Cb Support Cb Clamps & Nuts | As per relevent standard specification | 500 | EA | 6000
71 | 1 | SWR12101 | Painting of feeder name on support including cost of paint | Civil Work | Paint-Feeder Name on Support incl. Paint | As per relevent standard specification | 53 | EA | 53
72 | 2 | SMR40070 | Supply of Danger boards with clamps | Supply of Material | Supply of Danger boards with clamps | As per relevent standard specification | 116 | EA | 232
73 | 20 | SMR11485 | Supply of GI Flat 25X3 mm | Supply of Material | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 2100
74 | 32 | SWR12125 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete | Electrical work | Run-GI Earth Flat 25x3mm from metallic p | As per relevent standard specification | 14.03 | M | 448.96
75 | 1 | SWR11230 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Civil Work | Load-11/33KV XLPE UG Cable for all sizes | As per relevent standard specification | 1024 | DR | 1024
76 | 1 | SWR11231 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Civil Work | Unload-11/33KV XLPE UG Cable all sizes | As per relevent standard specification | 1024 | DR | 1024
77 | 4 | SWR11171 | Loading of 33/11KV XLPE UG Cable End Termination Kits for all sizes | Civil Work | Loading of 11/33 KV IN/OUT door kits | As per relevent standard specification | 6 | EA | 24
78 | 4 | SWR11152 | Un loading of 33/11KV XLPE UG Cable End Termination Kits for all sizes | Civil Work | Un-loading of 11/33 KV IN/OUT door kits | As per relevent standard specification | 4 | EA | 16
Total Service Cost: | [8 empty] | 2032094.07
GST 18%: | [8 empty] | 365776.9326
G. TOTAL: | [8 empty] | 2397871.0026
Assistant Engineer |  |  | Asst. Divisional Engineer |  |  | Divisional Engineer,
Construction/ Keesara |  |  | Construction-I/ Habsiguda |  |  | Construction, Habsiguda