## Schedule
SCHEDULE
Name of the Work :- Providing of interlinking line for 33kV MD Pally - Falaknuma, 33kV MD Pally-Aliabad & 33kV MD Pally-Kandikal Gate Feeders with laying of 0.7KM of 33kV 3X400Sq.mm XLPE UG Cable (Double Run) in Hyderabad South operation division of Hyderabad South Circle and the work executed by the Master Plan SD-III of Master plan Division-II in Master plan Hyderabad Circle under T&D Improvements to original works (Summer Action Plan 2026)
WBS Element :- T-2531-12-02-03-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 0.7 | Survey line&cabl inc peg mark,tree clear&trail pits | Elect | Labour | SWR22092 | 765 | KM | 535.5
2 | 5 | Loading of 11KV/33KV XLPE UG Cable Drums for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 5120
3 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators,transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)- Above 80 Km and upto 100 Km with Lorry for each trip | Elect | Labour | SWR11865 | 5839.5 | EA | 11679
4 | 5 | Un loading of 11KV/33KV XLPE UG Cable Drum for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 5120
5 | 700 | Excavation & laying of UG Cable (Double Run) - Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally 4" for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and liftetc - (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs &33 KV - 1.20 mtrs.- Along the CC / BT multi layer road requiring compressor - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11980 | 1388.84 | M | 972188
6 | 700 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 204.1 | M | 142870
7 | 100 | Raising of double run 33KV 3x400sqmm UG cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR12004 | 323.85 | M | 32385
8 | 6 | S&E-Smart RFID marker | Elect | Supply | SWR25089 | 2745 | EA | 16470
9 | 300 | Supply of 6" B class GI pipe 150 NB GI Pipe 4.85 mm thickness, 19.2 KG/Mtr | Elect | Supply | SMR40081 | 1344 | M | 403200
10 | 100 | supply of 6" DWC pipe | Elect | Supply | SMR11610 | 1012 | M | 101200
11 | 700 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 21000
12 | 16 | Making of 33KV 3X400Sq.mm XLPE UG Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 44236.16
13 | 4 | Making of 33KV 3X400Sq.mm XLPE UG Cable Straight through joints | Elect | Labour | SWR10382 | 5700.78 | EA | 22803.12
14 | 1.345 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 297.245
15 | 1.345 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 248.825
16 | 18 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1368
17 | 5.845 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 2408.6076
18 | 18 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 900
19 | 6 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 3075.3
20 | 12 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 13584
21 | 6 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 5944.08
22 | 3 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation and concreting - Erection of 33KV DP Structure with 175x85/150x75mm RS joist | Elect | Labour | SWR11276 | 5670 | SET | 17010
23 | 6 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | EA | 5568
24 | 6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation and concreting - RS Joists 150x75/175 x 85 mm | Elect | Labour | SWR10346 | 1934 |  | 11604
25 | 155 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 6355
26 | 9.54 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 62763.66
27 | 0.186 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893.01 | M3 | 724.0999
28 | 0.975 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 3340.35
29 | 3 | Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10239 | 126 | EA | 378
30 | 3 | Un loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10557 | 79 | EA | 237
31 | 3 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 13500
32 | 3 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 439.89
33 | 3 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 426
34 | 9 | Loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10266 | 41 | EA | 369
35 | 9 | Un loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10584 | 35 | EA | 315
36 | 3 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | SET | 2640
37 | 6 | Supply of CI eath pipe with 80mm dia,2.75 M Length | Elect | Supply | SMR11483 | 2789 | EA | 16734
38 | 6 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 7405.2
39 | 6 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 2316
40 | 3 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 159
41 | 30 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 3525
Total (Excl.GST) | [7 empty] | 1962442.0375
GST @ 18 % | [7 empty] | 353239.5667
Total (Incl. GST) | [7 empty] | 2315681.6042