## Aditya Schedule
Name of the work: Providing of 33KV alternate source to 33/11kV Aditya SS from 132/33kV Manikonda EHT SS by laying of 33KV 3X400sq.mm XLPE UG cable (Single Run) for a distance of 0.7KM from proposed DP Structure at Shaikpet main road to 33/11kV Aditya SS in Lines Asifnagar Section of Lines Asifnagar Sub Division in Mehdipatnam Operation Division and work executed by the Master plan SD-VI Sub-Division of MP-1 Division of Hyderabad Master plan Circle under T&D Improvements to original works (Summer Action Plan 2026).
WBS No : T-2531-12-01-03-01-003
SCHEDULE
S No. | Estimate Quantity (only FigurEs) | Item Detailed Specification Description | Work Type | Item Short Descripti | Service Code | Rate | UOM | Amount
1 | 0.7 | Survey line & cabel including peg mark & tree clearing | Electrical | Labour | SWR22092 | 765 | KM | 535.5 | SS LABOUR OLD
2 | 3 | Loading of 11KV/33KV XLPE UG Cable Drum for all sizes | Electrical | Labour | SWR11230 | 1024 | DR | 3072
3 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Upto 10 Km with Lorry for each trip | Electrical | Labour | SWR11860 | 2720.34 | EA | 5440.68
4 | 3 | Un loading of 11KV/33KV XLPE UG Cable Drum for all sizes | Electrical | Labour | SWR11231 | 1024 | DR | 3072
5 | 550 | Laying of 33 KV 3x400 Sqmm Single Run Cable XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Along the CC / BT multi layer road requiring compressor | Electrical | Labour | SWR11927 | 1175.56 | M | 646558
6 | 100 | Laying of 33 KV 3x400 Sqmm Single Run Cable XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Across the CC/ BT road crossing multi layer road requiring compressor wih hume pipe (excluding the cost of Hume Pipe) | Electrical | Labour | SWR11936 | 1319.84 | M | 131984
7 | 50 | Laying of 33 KV 3x400 Sqmm Single Run Cable XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road | Electrical | Labour | SWR11918 | 572.1 | M | 28605
8 | 10 | Supply & Erection of Smart RFID marker | Electrical | Labour | SWR25089 | 2745 | EA | 27450
9 | 5 | Making of 33KV 3X400Sq.mm XLPE UG Cable Straight through joints | Electrical | Labour | SWR10382 | 5700.78 | EA | 28503.9
10 | 200 | Supply of 6" B Class GI pipe 5mm thck 20Kg/M | Electrical | Supply | SMR40081 | 1344 | M | 268800
11 | 150 | Supply of 6" DWC pipe | Electrical | Supply | SMR11610 | 1012 | M | 151800
12 | 50 | Supply of Hume pipe 9" size | Electrical | Supply | SMR40001 | 125 | M | 6250
13 | 8 | Making of 33KV 3X400Sq.mm XLPE UG Cable Outdoor/Indoor End Termination | Electrical | Labour | SWR10387 | 2764.76 | EA | 22118.08
14 | 104 | Raising of single run 33kV 3x400 Sqmm Cu cable on already erected support with wooden / MS clamps and connecting it to over head line withcable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Electrical | Labour | SWR11954 | 135.66 | M | 14108.64
15 | 650 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Electrical | Labour | SWR21903 | 30 | M | 19500
16 | 0.85 | LOADING of MS Channel,Angles,Flats&Rods | Electrical | Labour | SWR10206 | 221 | TO | 187.85
17 | 0.85 | UNLOADING of MS Channel,Angles,Flats&Rod | Electrical | Labour | SWR10524 | 185 | TO | 157.25
18 | 12 | Loading of R.S. Joists 175 x 85 mm | Electrical | Labour | SWR10204 | 76 | EA | 912
19 | 3.85 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Electrical | Labour | SWR10132 | 412.08 | TO | 1586.508
20 | 12 | Un loading of R.S. Joists 175 x 85 mm | Electrical | Labour | SWR10522 | 50 | EA | 600
21 | 8 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Electrical | Labour | SWR10642 | 512.55 | EA | 4100.4
22 | 8 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Electrical | Labour | SWR10640 | 1132 | EA | 9056
23 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Electrical | Labour | SWR11040 | 990.68 | EA | 7925.44
24 | 4 | Erection of Box pole 9/10/11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical | Labour | SWR11266 | 2643.83 | EA | 10575.32
25 | 63.83 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 75x8mm / 75 x 12 mm | Electrical | Labour | SWR10918 | 50 | RMT | 3191.5
26 | 8.4 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Electrical | Labour | SWR10356 | 6579 | M3 | 55263.6
27 | 0.248 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Electrical | Labour | SWR11890 | 3892.98 | M3 | 965.459
28 | 0.55 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Electrical | Labour | SWR10869 | 3426 | TO | 1884.3
29 | 2 | Erection of 33 KV LAS station/Line type including earthing | Electrical | Labour | SWR10396 | 880 | SET | 1760
30 | 3 | Loading of 33KV 800 Amps AB Switch | Electrical | Labour | SWR10239 | 126 | EA | 378
31 | 3 | Un loading of 33KV 800 Amps AB Switch | Electrical | Labour | SWR10557 | 79 | EA | 237
32 | 3 | Erection of 33 KV AB Switch including alignment and earthing | Electrical | Labour | SWR10392 | 4500 | EA | 13500
33 | 6 | Supply of CI Pipe earthing 80mm dia 2.75m long | Electrical | Supply | SMR11483 | 2789 | EA | 16734
34 | 6 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and | Electrical | Labour | SWR10357 | 1234.2 | EA | 7405.2
35 | 6 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Electrical | Labour | SWR10359 | 386 | EA | 2316
36 | 7 | Supply of Pre-cast cable Joint markersSupply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Electrical | Supply | SMR40085 | 484 | EA | 3388
37 | 6 | Painting of feeder name on support including cost of paint | Electrical | Labour | SWR12101 | 53 | EA | 318
38 | 50 | Supply of GI Bolts & Nuts,Washers etc., | Electrical | Supply | SMR11488 | 117.5 | KG | 5875
39 | 3 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical | Labour | SWR10881 | 142 | EA | 426
40 | 3 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Electrical | Labour | SWR12331 | 146.63 | EA | 439.89
41 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erection of 5 Mts RS Joist (Bit) Pole including fixing of Pole Mounted Box | Electrical | Labour | SWR20863 | 1044.23 | EA | 4176.92
|  | Total (Excl. GST) | [5 empty] | 1511157.437 | 1511157.437
|  | 18% GST | [5 empty] | 272008.3387
Total Cost (Incl. GST) | [7 empty] | 1783165.7757 | 21881286.18 | -20098120.4043
|  |  | 2101655.95 |  |  |  |  | 33998770
9632925.29
|  |  | 5876135 |  |  |  |  | -32215604.2243
932746.63
18543462.87