## Final
Name of the Work:- Estimate for erection of 33/11KV sub-station, Construction of control room ,33KV & 11KV lines at Sikkindlapur village in Hathnoora Mandal of Jogipet Division in Sangareddy circle (WBS: S-1601-90-06-01-01-001)&(WBS: S-1601-90-07-01-01-001).
SNO | SSR Code | Estimate Quantity (Only figures) | Item Detailed Specification Description | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SWR10105 | 20 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevaent standard specifications | 600 | EA | 12000
2 | SWR10343 | 31 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevaent standard specifications | 2400 | EA | 74400
3 | SWR10356 | 27.28 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.76x0.76x1.52M with CC mix of ratio 1:3:6 Using form boxes (0.88 Cu.Mt)*31 with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevaent standard specifications | 6579 | M3 | 179475.12
4 | SWR11890 | 0.96 | ERECTION OF S.S. STRUCTURE: Coping of 0.45x0.45x0.45Mt with 1:8 slope Using form boxes (0.031Cumt.) | Civil work | Coping & Muffing-Iron Pole | As per relevaent standard specifications | 3893 | M3 | 3737.28
5 | SWR11331 | 31 | Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of poles with two coats of white cement (including cost of paint). | Electrical work | Paint-9.1M PSCC Poles as desc SSR | As per relevaent standard specifications | 485 | EA | 15035
6 | SWR11889 | 5.5 | Fabrication of 100 X 50mm MS Channel for formation of 11kV and 33kV bays: Fabrication and erection of M.S,Channel 100x50mm for forming of 33KV & 11 KV Bays as per standard specifications to facilitate stringing of bus, erection of LA sets, AB Switches bolts & Nuts etc. including painting with one coats of red oxide and two coats of Aluminium paint. GI bolts&nuts shall be used. | Electrical work | Fabr & Erect-MS Chnl 100x50mm for SS Bay | As per relevaent standard specifications | 6600 | TO | 36300
7 | SWR10404 | 115 | Erection of 33kV and 11kV Strung Bus with Panther (200Sqmm) ACSR Conductor: Erection of 33kV and 11kV Bus over the Substation structures with 200sqmm Panther ACSR conductor and giving Jumpers to connect the Switch gear by providing the suitable T clamps and round clamps suitable to Post type insulators & Insulators. | Electrical work | Stringing of bus with panther conductor | As per relevaent standard specifications | 327.68 | M | 37683.2
8 | SWR10392 | 2 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevaent standard specifications | 4500 | EA | 9000
9 | SWR10393 | 10 | Erection of 11kV AB Switches 800/400 Amps includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevaent standard specifications | 3200 | EA | 32000
10 | SWR11742 | 3 | Supply & erection of 11 kV 400 A convential single(1/3) phasing AB switches.includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | S&E-400A 11KV ABSwth Conv 1ph(1/3) in SS | As per relevaent standard specifications | 4232 | EA | 12696
11 | SWR21240 | 2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt). | Electrical work | Hoisting post ins&hrd wr 1panther 33kv | As per relevaent standard specifications | 781 | EA | 1562
12 | SWR21241 | 4 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Electrical work | Hoisting post ins&hrd wr 1panther 11kv | As per relevaent standard specifications | 507 | EA | 2028
13 | SWR10881 | 12 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical work | Painting AB switch OP rods with PO red | As per relevaent standard specifications | 142 | EA | 1704
14 | SWR23224 | 16.46 | Excavation of pit in all types of soils of size 2.2x2.2x0.85Mts.for Construction of Plinths for VCB (33KV & 11 KV ) | Earth work | Excavate-Pit for 33KV VCB | As per relevaent standard specifications | 331 | M3 | 5448.26
15 | SWR20685 | 22.24 | Providing of Base concreting (2.2x2.2x0.15 Mts) with 1:3:6 Concrete mix. Using form boxes, Providing of Concreting (2x2x1.0mts) with 1:3:6 Cocrete mix. Plastering of the plinth for smooth finishing with 12mm thick 1:3 cement motor and providing two coats white washing for part of the plinth above groung level. | Civil work | Cement concrete with 40MM metal VCB plin | As per relevaent standard specifications | 5160 | M3 | 114758.4
16 | SWR10461 | 4 | Erection of Switchgear complete for 11 kV VCB includes Assembling the VCB Structures and mounting the VCBs over the already erected foudation including wiring of Breaker Control Panel/CTs, erection of CTs and control pannel providing Jumpers. | Electrical work | Erection of 11kv VCB | As per relevaent standard specifications | 12000 | EA | 48000
17 | SWR10396 | 2 | Erection of 33KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 33kv LA stn type incl earthing | As per relevaent standard specifications | 880 | SET | 1760
18 | SWR10397 | 1 | Erection of 11 KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 11kv LA stn type incl earthing | As per relevaent standard specifications | 559 | SET | 559
19 | SWR10398 | 3 | Erection of 11 KV Lightening Arrestors line type complete including jumpering. | Electrical work | Erect of 11kvLA line type incl earthing | As per relevaent standard specifications | 505 | SET | 1515
20 | SMR11607 | 1 | Supply of 33kv HG fuse set including providing of jumpers | Electrical work | S-33KV HG Fuse Set excl Ins & Chnl | As per relevaent standard specifications | 6431 | SET | 6431
21 | SWR10394 | 1 | Erection of 33kv HG fuse set including providing of jumpers | Electrical work | Erect. of 33kv HG Fuseset incl earthing | As per relevaent standard specifications | 1331.81 | SET | 1331.81
22 | SMR11608 | 1 | Supply of 11kv HG fuse set including providing of jumpers | Electrical work | S-11KV HG Fuse Set | As per relevaent standard specifications | 1733.75 | SET | 1733.75
23 | SWR10395 | 1 | Erection of 11kv HG fuse set including providing of jumpers | Electrical work | Erect. of 11kv HG Fuseset incl earthing | As per relevaent standard specifications | 740.52 | SET | 740.52
24 | SMR11482 | 22 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevaent standard specifications | 3486 | EA | 76692
25 | SWR10357 | 22 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevaent standard specifications | 1234.2 | EA | 27152.4
26 | SWR10920 | 500 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification.75x8 mm MS flat for Earth mat and connecting to electrodes. | Electrical work | Laying of earth mat,excavation 75x 8mm | As per relevaent standard specifications | 65 | RMT | 32500
27 | SWR10919 | 950 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification. 50x6 mm MS flat for raisers, double flat shall be run for structure poles raisers & equipment earthing. | Electrical work | Earthing for raisers of SS Flat 50x6 mm. | As per relevaent standard specifications | 41 | RMT | 38950
28 | SMR40033 | 2 | Providing of double earthing for neutral with flexible copper jumpers of adequate size including arrangement by fixing M.S.Channel 100x50mm. | Electrical work | SupCU Flexi jumper for Power T/F Neutral | As per relevaent standard specifications | 4725 | EA | 9450
29 | SWR11771 | 4 | Erection of 24 Volts Battery along with Charger on the VCB plinth and giving DC supply to VCB's. | Electrical work | Erect-24V Batery with Chrgr incl grot-SS | As per relevaent standard specifications | 1050 | EA | 4200
30 | SWR11474 | 600 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable includes excavation of earth and back filling with sand and earth in alternate layers . The cable termination shall be made by providing proper size lugs and shall be identified with colours. | Electrical work | Laying-4 core cable | As per relevaent standard specifications | 15 | RMT | 9000
31 | SWR10463 | 1 | Erection of 25 KVA Three phase Station Transformer on the Substation Structures and giving jumpers/connections on HT side to the 11kV bus. Belting angle shall be provided both sides of DTR for securing DTR firmly in position. | Electrical work | Erection of Three Phase DTRs | As per relevaent standard specifications | 1139.95 | EA | 1139.95
32 | SMR40045 | 1 | Supply of AC Panel Board includes: Fixing of 1 No.100A, MCCB, 10kA capacity of any standard make including material cost. Fixing of suitable panel box 3x3x1 with M.S.Sheet of 16 SWG with front door compartments inclusive of material cost & powder coating (with C Channel ). Fabrication of panel Fixing of 96x96mm analog voltmeter with VSS switch Fixing of 20A HRC fuse Fixing of 3 phase supply indicator kwith HRC fuses Supply and fixing of 6 Sqmm copper flexible wire (PVC) Fixing of Stud type TBs for outgoing feeder Fixing of Epoxy bus supports. | Electrical work | Supply of AC Supply panel complete | As per relevaent standard specifications | 42000 | EA | 42000
33 | SMR40044 | 1 | Supply of DC Panel Board Fixing of suitable panel box of size 6'x6'x1' with M S sheet of 16 SWG with back doors (4'x6') and on front side with provision to fix up bakelite hylam sheet size of 4'x6' including cost of the panel with powder coating. Fixing of best quality of angles for panel. Fixing of C Channelfor panel. Fabrication of control panel including making suitable holes and board Fixing of Stud type TBs for outgoing feeder Fixing of 24V DC pilot lamps of standard make Fixing of healthy trip push buttons with LED lamp Fixing of plain switches for alarm acceptance and for PTR signal Fixing of ON/OFF push buttons Fixing of digital volt meter for 11kV Fixing of VSS of standard make, Fixing of Engraved AL plates for Alarm panel of various VCB Laying of 2.5Sqmm copper flexible wire for internal wiring . Fixing of digital frequency meter Fixing of Copper lugs and ferrules for internal wiring. Fixing of 4" Gang bells 24V DC Fixing of flow diagram with rading strip Fixing of HRC fuse units | Electrical work | Supply of DC Anunc.relay panel 8 feeders | As per relevaent standard specifications | 42500 | EA | 42500
34 | SWR11893 | 2 | Erection of control/Relay panels,ACPanels,announciation panel set cin the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | electrical work | Erect-Contrl/Relay, AC, Announ. Panels | As per relevaent standard specifications | 1930 | EA | 3860
35 | SWR10342 | 8 | Erection of 8.0 Mts PSCC Poles complete with necessary hard ware for yard lighting excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevaent standard specifications | 1500 | EA | 12000
36 | SWR10956 | 8 | Fixing of Metal halide/LED lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5M GI pipe complete. | Electrical work | Fixing of LED/Metal halide complete. | As per relevaent standard specifications | 1268 | EA | 10144
37 | SWR20028 | 8 | Supply and Fixing of junction box and Providing with proper Fuse protection and required glauds suitable for Cable Terminations. The box shall be fixed on the pole. | Electrical work | 33/11kv S.S Yard lighting junction box | As per relevaent standard specifications | 351.9 | EA | 2815.2
38 | SWR20526 | 1 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply & fixing of marshall box | As per relevaent standard specifications | 3085.5 | EA | 3085.5
39 | SMR40088 | 1 | Supply and fixing of filled sand bucket set complete (4 Nos. Buckets) with stand to mount fire buckets. | Electrical work | Sup Fire Buckets Stand with Buckets | As per relevaent standard specifications | 1386 | SET | 1386
40 | SMR40087 | 2 | Supply and fixing of CO2 Cylinder set as per IS2878 Specifications. | Electrical work | Sup TrollyMounted Co2 Cylinders(IS-2878) | As per relevaent standard specifications | 9240 | EA | 18480
41 | SWR11895 | 1 | Supplying and fixing of feeder indicator board to each of the 3Nos feeder breakers and LV breaker, danger boards made of 1'x1' and properly mounted on the structures. The letters written on the borad shall be 1.5"size with blue colour and background shall be of white colour | Electrical work | S&F-33/11KV SS Feeder Indicator Board | As per relevaent standard specifications | 551 | SET | 551
42 | SWR20032 | 1 | Supply and fixing of wooden board of size 3'x2'.5'indicating the layout of the Switch yard. | Electrical work | Sup &fix of board ind Switchyard layout | As per relevaent standard specifications | 1654 | EA | 1654
43 | SMR40086 | 1 | Supply and Erection of Permanent Name Board of on 3'x4' steel sheetmounted on steel frame as described in Specification. | Electrical work | Sup 33/11kv S.S Permanent name board | As per relevaent standard specifications | 10238 | EA | 10238
44 | SMR40076 | 1 | Supply of Digital clamp meter. | Electrical work | Supply of Digital clamp meter. | As per relevaent standard specifications | 2888 | EA | 2888
45 | SMR40064 | 1 | Supply of Rechargeable LED torch light of Standard make. | Electrical work | Sup Rechargeable LED torch light. | As per relevaent standard specifications | 1733 | EA | 1733
46 | SMR40063 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box containing ‘D’Spanners from size 6 to 54, Hammer small and big size, Ring spanners from 6 to 28, Adjustable spanner, Pipe wrench, Cutting Plier, Nose plier, Tester, insulated Screw drive. | Electrical work | SupTaparia Tool kit complete as per Spec | As per relevaent standard specifications | 4925 | SET | 4925
47 | SWR22090 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Electrical work | Sup& fix safety inst/SS Op. inst board | As per relevaent standard specifications | 2205 | EA | 2205
48 | SMR11598 | 8 | Supply of 25 W LED lamp with fitting of philips make | Electrical work | S-25W LED fixture set | As per relevaent standard specifications | 3200 | EA | 25600
49 | SMR12378 | 1 | Supply of Alluminum Ladder(20 feet) | Electrical work | S-10ft Aluminium Ladder | As per relevaent standard specifications | 1654 | EA | 1654
50 | SMR40075 | 1 | Supply of Megger (2000 ohms, 0-2.5kv) | Electrical work | Supply of Earth megger (1000v) | As per relevaent standard specifications | 8085 | EA | 8085
51 | SMR11599 | 4 | Supply of Earth Discharging Rod 10' length. | Electrical work | S-Earth Rod 8ft Long 3mm Thick | As per relevaent standard specifications | 1000 | EA | 4000
52 | SMR11488 | 450 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevaent standard specifications | 117.5 | KG | 52875
53 | SMR11591 | 66 | Supply of PG clamps for panther 2 bolted 800 A. | Electrical work | S-Al. alloy three bolted PG clamps 800A | As per relevaent standard specifications | 130 | EA | 8580
54 | SWR20029 | 350 | Supply and Laying of 2 core/4 core cable includes excavation earth and back filling with sand and earth in alternate layers as shown in the sketch. The cable termination shall be made by providing proper size of lugs at both ends of the cable termination. | Electrical work | 33/11kv S.S laying of 2/4core for light | As per relevaent standard specifications | 50 | M | 17500
55 | SWR20308 | 31 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevaent standard specifications | 407.29 | EA | 12625.99
56 | SWR20307 | 8 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevaent standard specifications | 271.52 | EA | 2172.16
57 | SWR11860 | 2 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip. | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevaent standard specifications | 2720.34 | EA | 5440.68
58 | SWR10150 | 10.5 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevaent standard specifications | 617.1 | TO | 6479.55
59 | SWR10206 | 10.5 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevaent standard specifications | 221 | TO | 2320.5
60 | SWR10524 | 10.5 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevaent standard specifications | 185 | TO | 1942.5
61 | SWR11220 | 350 | Loading and unwinding of Panther conductor. | Electrical work | Load-Unwinding Panther conductor | As per relevaent standard specifications | 3 | M | 1050
62 | SWR11221 | 350 | Unloading of Panther conductor. | Electrical work | Unload-Unwinding Panther conductor | As per relevaent standard specifications | 2 | M | 700
63 | SWR12416 | 2 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevaent standard specifications | 2 | KI | 4
64 | SWR10631 | 2 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevaent standard specifications | 2 | KI | 4
65 | SWR10618 | 2 | Loading of 33KV Metal parts bag of 25 nos. | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevaent standard specifications | 65 | BAG | 130
66 | SWR10632 | 2 | Unloading of 33 KV Metal parts bag of 25 nos. | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevaent standard specifications | 65 | BAG | 130
67 | SWR10212 | 2 | Loading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | LOADING of 11kv Pin/Post/Solid Core Insu | As per relevaent standard specifications | 1 | KI | 2
68 | SWR10530 | 2 | Unloading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | UNLOADING of 11kv Pin/Post/Solid Core In | As per relevaent standard specifications | 1 | KI | 2
69 | SWR11701 | 600 | Loading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | Load-PVC Control Cable 10C | As per relevaent standard specifications | 1 | M | 600
70 | SWR11712 | 600 | Unloading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | UnLoad-PVC Control Cable 10C | As per relevaent standard specifications | 1.02 | M | 612
71 | SWR11691 | 1 | Loading of 3Ph 25KVA Distribution Transformer. | Electrical work | Load-3Ph 25KVA DTR | As per relevaent standard specifications | 252 | EA | 252
72 | SWR11692 | 1 | UnLoading of 3Ph 25KVA Distribution Transformer. | Electrical work | UnLoad-3Ph 25KVA DTR | As per relevaent standard specifications | 202 | EA | 202
73 | SWR10200 | 1 | Loading of 33/11 KV Current Transformers/ Potential Transformers. | Electrical work | LOADING of 33/11 KV CTs/ PTs | As per relevaent standard specifications | 165 | EA | 165
74 | SWR10266 | 6 | Loading of 33 KV10 KA LAs Station type. | Electrical work | LOADING of 33 KV10 KA LAs Station type | As per relevaent standard specifications | 41 | EA | 246
75 | SWR10584 | 6 | Unloading of 33 KV10 KA LAs Station type. | Electrical work | UNLOADING of 33 KV10 KA LAs Station type | As per relevaent standard specifications | 35 | EA | 210
76 | SWR10265 | 9 | Loading of 11 KV10 KA LAs Line type. | Electrical work | LOADING of 11 KV, 10 KA LAs Line type | As per relevaent standard specifications | 32 | EA | 288
77 | SWR10583 | 9 | Unloading of 11 KV10 KA LAs Line type. | Electrical work | UNLOADING of 11 KV, 10 KA LAs Line type | As per relevaent standard specifications | 32 | EA | 288
78 | SWR10264 | 3 | Loading of 11 KV10 KA LAs Station type. | Electrical work | LOADING of 11 KV,10 KA LAs Station type | As per relevaent standard specifications | 32 | EA | 96
79 | SWR10582 | 3 | Unloading of 11 KV10 KA LAs Station type. | Electrical work | UNLOADING of 11 KV,10 KA LAs Station typ | As per relevaent standard specifications | 32 | EA | 96
80 | SWR10239 | 2 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevaent standard specifications | 126 | EA | 252
81 | SWR10557 | 2 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevaent standard specifications | 79 | EA | 158
82 | SWR10238 | 10 | loading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevaent standard specifications | 80 | EA | 800
83 | SWR10556 | 10 | Unloading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevaent standard specifications | 80 | EA | 800
84 | SWR11224 | 4 | Loading and Unloading of 12V/24V Battery Set. | Electrical work | Load/Unload-12V/24V Battery Set | As per relevaent standard specifications | 23 | EA | 92
85 | SWR10356 | 2.66 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.76x0.76x0.152M with CC mix of ratio 1:3:6 Using form boxes (0.087 Cu.Mt)*31 with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevaent standard specifications | 6579 | M3 | 17500.14
86 | SWR10402 | 1 | Erection of 11kv Potential Transformer sets complete including jumpering. The LV side of the PT shall be provided with proper fuse protection mounted in separate marshalling boxwith proper size cable glands etc. The box shall be mounted on the Substation structure. | Electrical work | Erection of 11kv three phase PT s | As per relevaent standard specifications | 800 | SET | 800
87 | SWR10518 | 1 | Unloading of 33/11 KV Current Transformers/ Potential Transformers | Electrical work | UNLOADING of 33/11 KV CTs/ PTs | As per relevaent standard specifications | 128 | EA | 128
88 | SWR10674 | 1 | Fixing of Distribution Box and Providing with proper Fuse protection system and reqired Cable Terminations at Station T/F LT side and AC/DC Panel and fixing meter. Power cable of adequate size shall be provided from station DTR to control room AC Panel. | Electrical work | Erection of LT distribution box | As per relevaent standard specifications | 1594.67 | EA | 1594.67
89 | SWR10356 | 4.32 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.6x0.6x1.5M with CC mix of ratio 1:3:6 Using form boxes (0.546 Cu.Mt)*8 with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevaent standard specifications | 6579 | M3 | 28421.28
90 | SWR21750 | 2 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply and fixing of PT Marshalling box | As per relevaent standard specifications | 1139.85 | EA | 2279.7
91 | SWR10110 | 19 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the hard pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated hard rock bits if any and leveling the site without any lead. | Earth work | EXCAV. OF PIT HARD (2.6" x 2.6" x 5.0') | As per relevaent standard specifications | 1440 | EA | 27360
92 | SMR40009 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for First coat of 1st GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 1st coat Al. Painting. | As per relevaent standard specifications | 2181 | TO | 11995.5
93 | SWR10877 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 1st coat of Aluminium | Electrical work | Labour for 1st coat Al. Painting. | As per relevaent standard specifications | 851 | TO | 4680.5
94 | SMR40010 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for second coat of 2nd GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 2nd coat Al. Painting. | As per relevaent standard specifications | 1293 | TO | 7111.5
95 | SWR10879 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 2nd coat of Aluminium | Electrical work | Labour for 2nd coat Al. Painting. | As per relevaent standard specifications | 482 | TO | 2651
96 | SWR22092 | 4.66 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 33 kv line | Earth work | survey line&cabl inc peg mark&tree clear | As per relevaent standard specifications | 765 | KM | 3564.9 | 33kv line
97 | SWR10105 | 74 | Excavation of Pole pits of size 0.76x0.76x1.52 for 11 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevaent standard specifications | 600 | EA | 44400
98 | SWR10110 | 20 | Excavation of Pole pits of size 0.76x0.76x1.52 for 11 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the hard pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated hard rock bits if any and leveling the site without any lead. | Earth work | EXCAV. OF PIT HARD (2.6" x 2.6" x 5.0') | As per relevaent standard specifications | 1440 | EA | 28800
99 | SWR10978 | 94 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevaent standard specifications | 4165.28 | EA | 391536.32
100 | SWR10343 | 44 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevaent standard specifications | 2400 | EA | 105600
101 | SWR10981 | 22 | Formation of 33 kv cut points (Vertical/Horizantal) including fixing of Clamps and top cleat and fixing of pin insulator complete with necessary hard wear for stud locations excluding the cost of pit Excavation and the pole shall be numbered with colour paint and earthing. | Electrical work | Horizontal Cut point for 33 KV line | As per relevaent standard specifications | 1759.5 | EA | 38709
102 | SWR10356 | 65.176 | Concreting the location after erection of 11/9.1 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.75X0.75X2 Mts)* 48 = 54Cu.Mt and (0.45X0.45X1.265 Mts)* 44 = 11.176 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevaent standard specifications | 6579 | M3 | 428792.904
103 | SWR10366 | 4.66 | Paving of the 100 sqmm AAA conductor and stringing duly arranging temporary guys, tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pin binding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Earth work | Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevaent standard specifications | 12600.06 | KM | 58716.2796
104 | SMR11488 | 188 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevaent standard specifications | 117.5 | KG | 22090
105 | SWR11180 | 94 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevaent standard specifications | 431.97 | EA | 40605.18
106 | SWR20308 | 44 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevaent standard specifications | 407.29 | EA | 17920.76
107 | SWR10191 | 4 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevaent standard specifications | 202 | EA | 808
108 | SWR10509 | 4 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevaent standard specifications | 100 | EA | 400
109 | SWR11860 | 4 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip. | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevaent standard specifications | 2720.34 | EA | 10881.36
110 | SWR10150 | 1.05 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevaent standard specifications | 617.1 | TO | 647.955
111 | SWR10206 | 1.05 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevaent standard specifications | 221 | TO | 232.05
112 | SWR10524 | 1.05 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevaent standard specifications | 185 | TO | 194.25
113 | SWR10211 | 47 | Loading of 33 KV Pin insulators | Electrical work | LOADING of 33 KV Pin insulators | As per relevaent standard specifications | 3 | KI | 141
114 | SWR10529 | 47 | Unloading of 33 KV Pin insulators | Electrical work | UNLOADING of 33 KV Pin insulators | As per relevaent standard specifications | 3 | KI | 141
115 | SWR12416 | 22 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevaent standard specifications | 2 | KI | 44
116 | SWR10631 | 22 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevaent standard specifications | 2 | KI | 44
117 | SWR10618 | 7 | Loading of 33KV Metal parts bag of 25 nos. | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevaent standard specifications | 65 | BAG | 455
118 | SWR10632 | 7 | Unloading of 33 KV Metal parts bag of 25 nos. | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevaent standard specifications | 65 | BAG | 455
119 | SWR10354 | 22 | Erection of 33 kv Stay set complete including fixing of bow ,fixing and binding of Eye bolt, Anchor rod, guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. | Electrical work | Assembly and erection of Stay set 33kv | As per relevaent standard specifications | 684.53 | SET | 15059.66
120 | SWR21190 | 66 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In all soils except Hard gravel Hard Murram, Disintegrated Rock,Hard rock Requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevaent standard specifications | 520 | EA | 34320
121 | SWR10319 | 115 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 75 x 8 mm MS Flat | Earth work | Fab Back clamps with 75 x 8 mm MS Flat | As per relevaent standard specifications | 31 | EA | 3565
122 | SWR10322 | 88 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 75 x 8 mm MS Flat | Electrical work | Fab Stay clamps with 75x8 mm MM Flat | As per relevaent standard specifications | 42 | EA | 3696
123 | SWR10378 | 138 | Numbering of poles incl. cost of paint | Electrical work | Numbering of poles incl. cost of paint | As per relevaent standard specifications | 32 | EA | 4416
124 | SWR10356 | 5.63 | Concreting the stay location after erection of 11 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / stay set .Using form boxes (0.45X0.45X1.265 Mts)* 22 = 5.63 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevaent standard specifications | 6579 | M3 | 37039.77
125 | SWR22092 | 5.22 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 11 kv line | Earth work | survey line&cabl inc peg mark&tree clear | As per relevaent standard specifications | 765 | KM | 3993.3 | 11kv line
126 | SWR10105 | 73 | Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevaent standard specifications | 600 | EA | 43800
127 | SWR10110 | 30 | Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the hard pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated hard rock bits if any and leveling the site without any lead. | Earth work | EXCAV. OF PIT HARD (2.6" x 2.6" x 5.0') | As per relevaent standard specifications | 1440 | EA | 43200
128 | SWR10342 | 38 | Erection of 8.0 Mts PSCC Poles complete with necessary hard ware for yard lighting excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevaent standard specifications | 1500 | EA | 57000
129 | SWR10343 | 103 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevaent standard specifications | 2400 | EA | 247200
130 | SWR10653 | 22 | Formation of 11 kv cut points (Vertical/Horizantal) including fixing of 11 KV Cross arms,clamps, strain insulators sets complete with hardware and stays (Bows and Eye-bolts), Excluding the cost of pit Excavation and pole erection. The contractor has to supply GI Bolts and Nuts. | Electrical work | Formatn of Horiz Cut point for 11KV line | As per relevaent standard specifications | 1350 | EA | 29700
131 | SWR10356 | 42.973 | Concreting the location after erection of 9.1 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.76X0.76X1.52 Mts)* 38 = 33.32 Cu.Mt and (0.45X0.45X1.265 Mts)* 38 = 9.728 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevaent standard specifications | 6579 | M3 | 282719.367
132 | SWR10365 | 5.22 | Paving of the conductor 55 Sqmm Single Circuit (3 Conductors) AAAC and stringing duly arranging temporary guys,tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pinbinding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing of 55sqmm 33/11kv Line 3 Cond | As per relevaent standard specifications | 8500 | KM | 44370
133 | SMR11488 | 200 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevaent standard specifications | 117.5 | KG | 23500
134 | SWR10206 | 1.04 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevaent standard specifications | 221 | TO | 229.84
135 | SWR10524 | 1.04 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevaent standard specifications | 185 | TO | 192.4
136 | SWR11248 | 309 | Loading 11KV Polymer Pin Insulator with GI pins | Electrical work | Load-11KV Polymer Pin Insulator-GI pin | As per relevaent standard specifications | 1 | EA | 309
137 | SWR11249 | 309 | Unloading 11KV Polymer Pin Insulator with GI pins | Electrical work | Unload-11KV Polymer Pin Insulator-GI pin | As per relevaent standard specifications | 1 | EA | 309
138 | SWR10134 | 1.04 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevaent standard specifications | 587.52 | TO | 611.0208
139 | SWR11862 | 3 | Transport of VCB , Control pannels, current transformater, bosster etc, above 20 KM and upto 30 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs >20 & <30Km | As per relevaent standard specifications | 3691.38 | EA | 11074.14
140 | SWR10191 | 3 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevaent standard specifications | 202 | EA | 606
141 | SWR10509 | 3 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevaent standard specifications | 100 | EA | 300
142 | SWR20307 | 38 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevaent standard specifications | 271.52 | EA | 10317.76
143 | SWR20308 | 103 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevaent standard specifications | 407.29 | EA | 41950.87
144 | SWR10228 | 84 | Loading of 11 KV V - Cross arms | Electrical work | LOADING of 11 KV V - Cross arms | As per relevaent standard specifications | 4 | EA | 336
145 | SWR10546 | 84 | Unloading of 11 KV V - Cross arms | Electrical work | UNLOADING of 11 KV V - Cross arms | As per relevaent standard specifications | 4 | EA | 336
146 | SWR12402 | 7 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevaent standard specifications | 48 | BAG | 336
147 | SWR12421 | 7 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevaent standard specifications | 48 | BAG | 336
148 | SWR10251 | 84 | Loading of 11 KV Top fittings | Electrical work | LOADING of 11 KV Top fittings | As per relevaent standard specifications | 1 | EA | 84
149 | SWR10569 | 84 | Unloading of 11 KV Top fittings | Electrical work | UNLOADING of 11 KV Top fittings | As per relevaent standard specifications | 1 | EA | 84
150 | SWR12416 | 9 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevaent standard specifications | 2 | KI | 18
151 | SWR10631 | 9 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevaent standard specifications | 2 | KI | 18
152 | SWR10353 | 19 | Erection of 11 kv Stay set complete including fixing of bow, fixing and binding of Eye bolt,Anchor rod,guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. The contractor has to supply GI Bolts and Nuts. | Earth work | Assembly and erection of Stay set11kv&LT | As per relevaent standard specifications | 606.85 | SET | 11530.15
153 | SWR21190 | 57 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In all soils except Hard gravel Hard Murram, Disintegrated Rock,Hard rock Requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevaent standard specifications | 520 | EA | 29640
154 | SWR10320 | 42 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 50 x 6 mm MS Flat | Electrical work | Fab Back clamps with 50 x 6 mm MS Flat | As per relevaent standard specifications | 15 | EA | 630
155 | SWR10323 | 32 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 50 x 6 mm MS Flat | Electrical work | Fab Stay clamps with 50 x 6 mm MS Flat | As per relevaent standard specifications | 25 | EA | 800
156 | SWR10378 | 141 | Numbering of poles incl. cost of paint | Electrical work | Numbering of poles incl. cost of paint | As per relevaent standard specifications | 32 | EA | 4512
157 | SWR10356 | 4.8 | Concreting the stay location after erection of 9.1 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / stay set .Using form boxes (0.45X0.45X1.265 Mts)* 19 = 4.8 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevaent standard specifications | 6579 | M3 | 31579.2
158 | SWR10392 | 2 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevaent standard specifications | 4500 | EA | 9000 | DP Str
159 | SWR10105 | 4 | Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevaent standard specifications | 600 | EA | 2400
160 | SWR10342 | 8 | Erection of 8.0 Mts PSCC Poles complete with necessary hard ware for yard lighting excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevaent standard specifications | 1500 | EA | 12000
161 | SWR10343 | 4 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevaent standard specifications | 2400 | EA | 9600
162 | SWR10356 | 5.55 | Concreting the location after erection of 9.1/8 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.76X0.76X1.52 Mts)* 4 = 3.508Cu.Mt and (0.45X0.45X1.265 Mts)* 8 = 2.048 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevaent standard specifications | 6579 | M3 | 36513.45
163 | SMR11488 | 5 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevaent standard specifications | 117.5 | KG | 587.5
164 | SWR10206 | 0.67 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevaent standard specifications | 221 | TO | 148.07
165 | SWR10524 | 0.67 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevaent standard specifications | 185 | TO | 123.95
166 | SWR10134 | 0.67 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevaent standard specifications | 587.52 | TO | 393.6384
167 | SWR20307 | 8 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevaent standard specifications | 271.52 | EA | 2172.16
168 | SWR20308 | 4 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevaent standard specifications | 407.29 | EA | 1629.16
169 | SWR12402 | 1 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevaent standard specifications | 48 | BAG | 48
170 | SWR12421 | 1 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevaent standard specifications | 48 | BAG | 48
171 | SWR12416 | 1 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevaent standard specifications | 2 | KI | 2
172 | SWR10631 | 1 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevaent standard specifications | 2 | KI | 2
173 | SMR11482 | 4 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevaent standard specifications | 3486 | EA | 13944
174 | SWR10357 | 4 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevaent standard specifications | 1234.2 | EA | 4936.8
175 | SMR11485 | 60 | Supply of earthing GI Flat 25X3 mm including material | Earth work | S-Earthing GI flat 25x3 mm incl material | As per relevaent standard specifications | 105 | KG | 6300
176 | SWR10239 | 2 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevaent standard specifications | 126 | EA | 252
177 | SWR10557 | 2 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevaent standard specifications | 79 | EA | 158
178 | SWR21190 | 8 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In all soils except Hard gravel Hard Murram, Disintegrated Rock,Hard rock Requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevaent standard specifications | 520 | EA | 4160
179 | SWR10393 | 3 | Erection of 11kV AB Switches 800/400 Amps includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevaent standard specifications | 3200 | EA | 9600 | 11kv ABS
180 | SMR11488 | 10 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevaent standard specifications | 117.5 | KG | 1175
181 | SWR10206 | 0.26 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevaent standard specifications | 221 | TO | 57.46
182 | SWR10524 | 0.26 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevaent standard specifications | 185 | TO | 48.1
183 | SWR10134 | 0.26 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevaent standard specifications | 587.54 | TO | 152.7604
184 | SMR11484 | 3 | Supply of C I earth pipe of size 50mm dia, 2 mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 50mm dia 2m long | As per relevaent standard specifications | 2441 | EA | 7323
185 | SWR11222 | 6 | Loading/Unloading of C I earth pipe of size 80/50mm dia, 2 mtrs long for earth electrode | Electrical work | Load/Unload-CI pipe 80/50 mm dia 2mt L | As per relevaent standard specifications | 18 | EA | 108
186 | SWR34671 | 3 | Providing of collar rings of 450mm dia at 4 pole structure | Electrical work | Collar/ Rings of 450mm dia | As per relevaent standard specifications | 250 | EA | 750
187 | SMR11485 | 30 | Supply of earthing GI Flat 25X3 mm including material | Earth work | S-Earthing GI flat 25x3 mm incl material | As per relevaent standard specifications | 105 | KG | 3150
188 | SWR10238 | 3 | loading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevaent standard specifications | 80 | EA | 240
189 | SWR10556 | 3 | Unloading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevaent standard specifications | 80 | EA | 240
190 | SWR22092 | 2.46 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 33 kv line | Earth work | survey line&cabl inc peg mark&tree clear | As per relevaent standard specifications | 765 | KM | 1881.9 | 33kv ALTER line
191 | SWR10105 | 35 | Excavation of Pole pits of size 0.75x0.75x2 for 11 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevaent standard specifications | 600 | EA | 21000
192 | SWR10110 | 15 | Excavation of Pole pits of size 0.75x0.75x2 for 11 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the hard pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated hard rock bits if any and leveling the site without any lead. | Earth work | EXCAV. OF PIT HARD (2.6" x 2.6" x 5.0') | As per relevaent standard specifications | 1440 | EA | 21600
193 | SWR10978 | 50 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevaent standard specifications | 4165.28 | EA | 208264
194 | SWR10343 | 30 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevaent standard specifications | 2400 | EA | 72000
195 | SWR10981 | 16 | Formation of 33 kv cut points (Vertical/Horizantal) including fixing of Clamps and top cleat and fixing of pin insulator complete with necessary hard wear for stud locations excluding the cost of pit Excavation and the pole shall be numbered with colour paint and earthing. | Electrical work | Horizontal Cut point for 33 KV line | As per relevaent standard specifications | 1759.5 | EA | 28152
196 | SWR10356 | 38.05 | Concreting the location after erection of 11/9.1 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.75X0.75X2 Mts)* 27 = 30.37Cu.Mt and (0.45X0.45X1.265 Mts)* 30 = 7.68 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevaent standard specifications | 6579 | M3 | 250330.95
197 | SWR10366 | 2.46 | Paving of the 100 sqmm AAA conductor and stringing duly arranging temporary guys, tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pin binding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Earth work | Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevaent standard specifications | 12600.06 | KM | 30996.1476
198 | SMR11488 | 100 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevaent standard specifications | 117.5 | KG | 11750
199 | SWR11180 | 50 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevaent standard specifications | 431.97 | EA | 21598.5
200 | SWR20308 | 30 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevaent standard specifications | 407.29 | EA | 12218.7
201 | SWR10191 | 2 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevaent standard specifications | 202 | EA | 404
202 | SWR10509 | 2 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevaent standard specifications | 100 | EA | 200
203 | SWR11860 | 2 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip. | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevaent standard specifications | 2720.34 | EA | 5440.68
204 | SWR10150 | 0.775 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevaent standard specifications | 617.1 | TO | 478.2525
205 | SWR10206 | 0.775 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevaent standard specifications | 221.01 | TO | 171.2827
206 | SWR10524 | 0.775 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevaent standard specifications | 185.01 | TO | 143.3827
207 | SWR10211 | 26 | Loading of 33 KV Pin insulators | Electrical work | LOADING of 33 KV Pin insulators | As per relevaent standard specifications | 3 | KI | 78
208 | SWR10529 | 26 | Unloading of 33 KV Pin insulators | Electrical work | UNLOADING of 33 KV Pin insulators | As per relevaent standard specifications | 3 | KI | 78
209 | SWR12416 | 17 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevaent standard specifications | 2 | KI | 34
210 | SWR10631 | 17 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevaent standard specifications | 2 | KI | 34
211 | SWR10618 | 4 | Loading of 33KV Metal parts bag of 25 nos. | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevaent standard specifications | 65 | BAG | 260
212 | SWR10632 | 4 | Unloading of 33 KV Metal parts bag of 25 nos. | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevaent standard specifications | 65 | BAG | 260
213 | SWR10354 | 10 | Erection of 33 kv Stay set complete including fixing of bow ,fixing and binding of Eye bolt, Anchor rod, guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. | Electrical work | Assembly and erection of Stay set 33kv | As per relevaent standard specifications | 684.53 | SET | 6845.3
214 | SWR21190 | 40 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In all soils except Hard gravel Hard Murram, Disintegrated Rock,Hard rock Requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevaent standard specifications | 520 | EA | 20800
215 | SWR10322 | 90 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 75 x 8 mm MS Flat | Electrical work | Fab Stay clamps with 75x8 mm MM Flat | As per relevaent standard specifications | 42 | EA | 3780
216 | SWR10378 | 80 | Numbering of poles incl. cost of paint | Electrical work | Numbering of poles incl. cost of paint | As per relevaent standard specifications | 32 | EA | 2560
217 | SWR10356 | 2.56 | Concreting the stay location after erection of 11 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / stay set .Using form boxes (0.45X0.45X1.265 Mts)* 10 = 2.56 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevaent standard specifications | 6579 | M3 | 16842.24
218 | SWR10392 | 3 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevaent standard specifications | 4500 | EA | 13500 | 4 POLE
219 | SWR10107 | 4 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevaent standard specifications | 700 | EA | 2800
220 | SWR10978 | 4 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevaent standard specifications | 4165.28 | EA | 16661.12
221 | SWR10105 | 8 | Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevaent standard specifications | 600 | EA | 4800
222 | SWR10343 | 8 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevaent standard specifications | 2400 | EA | 19200
223 | SWR10356 | 6.54 | Concreting the location after erection of 11/9.1 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.75X0.75X2 Mts)* 4 = 4.5Cu.Mt and (0.45X0.45X1.265 Mts)* 8 = 2.048 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevaent standard specifications | 6579 | M3 | 43026.66
224 | SMR11488 | 20 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevaent standard specifications | 117.5 | KG | 2350
225 | SWR10206 | 1 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevaent standard specifications | 221 | TO | 221
226 | SWR10524 | 1 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevaent standard specifications | 185 | TO | 185
227 | SWR10134 | 1 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevaent standard specifications | 587.52 | TO | 587.52
228 | SWR20308 | 8 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevaent standard specifications | 407.29 | EA | 3258.32
229 | SWR11180 | 4 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevaent standard specifications | 431.97 | EA | 1727.88
230 | SWR12402 | 1 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevaent standard specifications | 48 | BAG | 48
231 | SWR12421 | 1 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevaent standard specifications | 48 | BAG | 48
232 | SWR12416 | 2 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevaent standard specifications | 2 | KI | 4
233 | SWR10631 | 2 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevaent standard specifications | 2 | KI | 4
234 | SMR11482 | 6 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevaent standard specifications | 3486 | EA | 20916
235 | SWR10357 | 6 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevaent standard specifications | 1234.2 | EA | 7405.2
236 | SMR11485 | 50 | Supply of earthing GI Flat 25X3 mm including material | Earth work | S-Earthing GI flat 25x3 mm incl material | As per relevaent standard specifications | 105 | KG | 5250
237 | SWR10239 | 3 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevaent standard specifications | 126 | EA | 378
238 | SWR10557 | 3 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevaent standard specifications | 79 | EA | 237
239 | SWR34179 | 12 | Hire-JCB to Level & Clear the Site | Civil work | Hire-JCB to Level & Clear the Site | As per relevaent standard specifications | 2165.7 | H | 25988.4 | CIVIL
240 | SWR33015 | 96.7 | Excavation in Ordinary Soil | Civil work | Excavation in Ordinary Soil | As per relevaent standard specifications | 366 | M3 | 35392.2
241 | SWR33028 | 18.2 | PCC with 40mm Metal (1:4:8) | Civil work | PCC with 40mm Metal (1:4:8) | As per relevaent standard specifications | 4058 | M3 | 73855.6
242 | SWR33041 | 116.3 | CRS Masonary CM(1:6) 2nd Sort | Civil work | CRS Masonary CM(1:6) 2nd Sort | As per relevaent standard specifications | 4083 | M3 | 474852.9
243 | SWR33068 | 23.1 | Brick Masonary in CM(1:6) GFloor | Civil work | Brick Masonary in CM(1:6) GFloor | As per relevaent standard specifications | 8103 | M3 | 187179.3
244 | SWR33052 | 695 | S&Filling with Borrowed Gravel | Civil work | S&Filling with Borrowed Gravel | As per relevaent standard specifications | 485 | M3 | 337075
245 | SWR33098 | 5.9 | RCC Footing: M20Gr, Steel Centering | Civil work | RCC Footing: M20Gr, Steel Centering | As per relevaent standard specifications | 8306 | M3 | 49005.4
246 | SWR33100 | 2.8 | RCC Column GF: M20Gr, Steel Centering | Civil work | RCC Column GF: M20Gr, Steel Centering | As per relevaent standard specifications | 11181 | M3 | 31306.8
247 | SWR33099 | 2.6 | RCC Plinth Beam: M20Gr, Steel Centering | Civil work | RCC Plinth Beam: M20Gr, Steel Centering | As per relevaent standard specifications | 10923 | M3 | 28399.8
248 | SWR33107 | 0.7 | RCC Lintel GF: M20Gr, Steel Centering | Civil work | RCC Lintel GF: M20Gr, Steel Centering | As per relevaent standard specifications | 11372 | M3 | 7960.4
249 | SWR33114 | 13.5 | RCC Sunshade GF: M20Gr, Steel Centering | Civil work | RCC Sunshade GF: M20Gr, Steel Centering | As per relevaent standard specifications | 1210 | M2 | 16335
250 | SWR33121 | 2.9 | RCC Roof Beam GF: M20Gr, Steel Centering | Civil work | RCC Roof Beam GF: M20Gr, Steel Centering | As per relevaent standard specifications | 10982 | M3 | 31847.8
251 | SWR33128 | 10.2 | RCC Roof Slab GF: M20Gr, Steel Centering | Civil work | RCC Roof Slab GF: M20Gr, Steel Centering | As per relevaent standard specifications | 10496 | M3 | 107059.2
252 | SWR33144 | 2.5 | Reinforcement Steel Fe 415/500 | Civil work | Reinforcement Steel Fe 415/500 | As per relevaent standard specifications | 72726 | TON | 181815
253 | SWR33163 | 404.66 | Plastering 20mm (16mm+4mm)GFloor | Civil work | Plastering 20mm (16mm+4mm)GFloor | As per relevaent standard specifications | 422 | M2 | 170766.52
254 | SWR33184 | 124.2 | Raised Pointing to CRS Masonary CM(1:3) | Civil work | Raised Pointing to CRS Masonary CM(1:3) | As per relevaent standard specifications | 95 | M2 | 11799
255 | SWR33156 | 78.1 | Impervious Coat 20mm CM(1:3) GFloor | Civil work | Impervious Coat 20mm CM(1:3) GFloor | As per relevaent standard specifications | 450 | M2 | 35145
256 | SWR33264 | 5.7 | S&F MT Wood Frame & Door-Laminate | Civil work | S&F MT Wood Frame & Door-Laminate | As per relevaent standard specifications | 6871 | M2 | 39164.7
257 | SWR33278 | 5.76 | S&F Powder Coated Al Window | Civil work | S&F Powder Coated Al Window | As per relevaent standard specifications | 3572 | M2 | 20574.72
258 | SWR33310 | 6.25 | S&F of MS Safety Grill | Civil work | S&F of MS Safety Grill | As per relevaent standard specifications | 2622 | M2 | 16387.5
259 | SWR33219 | 39.2 | Polished Shabad Flooring 20mm CM(1:3) | Civil work | Polished Shabad Flooring 20mm CM(1:3) | As per relevaent standard specifications | 534 | M2 | 20932.8
260 | SWR33236 | 10.7 | Polished Shabad Skirting CM(1:3) | Civil work | Polished Shabad Skirting CM(1:3) | As per relevaent standard specifications | 603 | M2 | 6452.1
261 | SWR33029 | 25.2 | PCC with 40mm Metal (1:3:6) | Civil work | PCC with 40mm Metal (1:3:6) | As per relevaent standard specifications | 4336 | M3 | 109267.2
262 | SWR33030 | 5.1 | PCC with 20mm Metal (1:2:4) | Civil work | PCC with 20mm Metal (1:2:4) | As per relevaent standard specifications | 5469 | M3 | 27891.9
263 | SWR33057 | 49.5 | S&Spreading of 20mm HBG Metal | Civil work | S&Spreading of 20mm HBG Metal | As per relevaent standard specifications | 1618 | M3 | 80091
264 | SWR33403 | 110 | S&F MS Security Fencing Mesh (2"X2") | Civil work | S&F MS Security Fencing Mesh (2"X2") | As per relevaent standard specifications | 2108 | M2 | 231880
265 | SWR33404 | 10.55 | S&F MS Gate | Civil work | S&F MS Gate | As per relevaent standard specifications | 4676.9 | M2 | 49341.295
266 | SWR33333 | 121.2 | Painting with OBD 2Coats+Primer | Civil work | Painting with OBD 2Coats+Primer | As per relevaent standard specifications | 115 | M2 | 13938
267 | SWR33336 | 178.4 | Painting SnowCem/Apex 2 Coats+Primer | Civil work | Painting SnowCem/Apex 2 Coats+Primer | As per relevaent standard specifications | 205 | M2 | 36572
268 | SWR33329 | 175.9 | Painting with SuryaCem of 3 Coat | Civil work | Painting with SuryaCem of 3 Coat | As per relevaent standard specifications | 73 | M2 | 12840.7
269 | SWR33442 | 30 | S&F Conceal PVC Pipe 25mm dia in Slab | Civil work | S&F Conceal PVC Pipe 25mm dia in Slab | As per relevaent standard specifications | 90 | M | 2700
270 | SWR33441 | 20 | S&F Conceal PVC Pipe 25mm dia in Wall | Civil work | S&F Conceal PVC Pipe 25mm dia in Wall | As per relevaent standard specifications | 93 | M | 1860
271 | SWR33457 | 15 | S&F Modular Switch LP,FP,EFP for NRBuild | Civil work | S&F Modular Switch LP,FP,EFP for NRBuild | As per relevaent standard specifications | 602 | EA | 9030
272 | SWR33461 | 2 | S&F Modular 3/2pin 6A Sockets | Civil work | S&F Modular 3/2pin 6A Sockets | As per relevaent standard specifications | 493 | EA | 986
273 | SWR33464 | 2 | S&F Modular 3pin 16/6A Sockets | Civil work | S&F Modular 3pin 16/6A Sockets | As per relevaent standard specifications | 455 | EA | 910
274 | SWR33484 | 4 | S&F Batten Holder | Civil work | S&F Batten Holder | As per relevaent standard specifications | 224 | EA | 896
275 | SWR33545 | 4 | S&F 20W LED Retro Tube Light | Civil work | S&F 20W LED Retro Tube Light | As per relevaent standard specifications | 876.5 | EA | 3506
276 | SWR33494 | 90 | S&R 2 of 14/0.3mm (1.0sqmm) (FR) | Civil work | S&R 2 of 14/0.3mm (1.0sqmm) (FR) | As per relevaent standard specifications | 49 | M | 4410
277 | SWR33497 | 30 | S&R 2 of 36/0.3mm (2.5sqmm) (FR) | Civil work | S&R 2 of 36/0.3mm (2.5sqmm) (FR) | As per relevaent standard specifications | 100 | M | 3000
278 | SWR33520 | 1 | S&F 8wySPNDB IP-20,10kA-6-32A SPMCB 4No | Civil work | S&F 8wySPNDB IP-20,10kA-6-32A SPMCB 4No | As per relevaent standard specifications | 5368 | EA | 5368
279 | SWR33596 | 1 | Provd-Independent Earthing | Civil work | Provd-Independent Earthing | As per relevaent standard specifications | 5169 | EA | 5169
280 | SWR33597 | 15 | S&R No.8 SWG Copper Wire | Civil work | S&R No.8 SWG Copper Wire | As per relevaent standard specifications | 153 | M | 2295
281 | SWR33563 | 2 | S&F 1200mm (48'') Sweep Ceiling Fan | Civil work | S&F 1200mm (48'') Sweep Ceiling Fan | As per relevaent standard specifications | 2225 | EA | 4450
282 | SWR33224 | 13.7 | Ceramic Tile Flooring 20mm CM(1:3) | Civil work | Ceramic Tile Flooring 20mm CM(1:3) | As per relevaent standard specifications | 949 | M2 | 13001.3
283 | SWR34311 | 1 | S&F Orissa Pan WC 580mmx440mm | Civil work | S&F Orissa Pan WC 580mmx440mm | As per relevaent standard specifications | 2207 | EA | 2207
284 | SWR34386 | 2 | S&F Floor Trap (Bell Mouth) 110mm | Civil work | S&F Floor Trap (Bell Mouth) 110mm | As per relevaent standard specifications | 269 | EA | 538
285 | SWR34382 | 2 | S&F 90mm dia Plain Bend PVC/SWR Pipe | Civil work | S&F 90mm dia Plain Bend PVC/SWR Pipe | As per relevaent standard specifications | 84 | EA | 168
286 | SWR34385 | 1 | S&F 75mm dia Door Bend PVC/SWR Pipe | Civil work | S&F 75mm dia Door Bend PVC/SWR Pipe | As per relevaent standard specifications | 81 | EA | 81
287 | SWR34286 | 1 | S&F 150mmx100mm SWG Gully Trap | Civil work | S&F 150mmx100mm SWG Gully Trap | As per relevaent standard specifications | 749 | EA | 749
288 | SWR34377 | 6 | S&F 110mm dia 3M 1Socket PVC/SWR Pipe | Civil work | S&F 110mm dia 3M 1Socket PVC/SWR Pipe | As per relevaent standard specifications | 428 | M | 2568
289 | SWR34453 | 1 | S&F 4" dia PVC Cowl | Civil work | S&F 4" dia PVC Cowl | As per relevaent standard specifications | 23 | EA | 23
290 | SWR34444 | 1 | Construct- 4' dia & 5' Ht Soak Pit | Civil work | Construct- 4' dia & 5' Ht Soak Pit | As per relevaent standard specifications | 4904 | EA | 4904
291 | SWR34362 | 100 | S&F 22.20mm OD CPVC Pipe-SDR 11 | Civil work | S&F 22.20mm OD CPVC Pipe-SDR 11 | As per relevaent standard specifications | 417 | M | 41700
292 | SWR34363 | 100 | S&F 28.60mm OD CPVC Pipe-SDR 11 | Civil work | S&F 28.60mm OD CPVC Pipe-SDR 11 | As per relevaent standard specifications | 514 | M | 51400
293 | SWR34344 | 24 | S&F-15mm GM/Bronze Ball Valve | Civil work | S&F-15mm GM/Bronze Ball Valve | As per relevaent standard specifications | 230 | EA | 5520
294 | SWR34345 | 1 | S&F-20mm GM/Bronze Ball Valve | Civil work | S&F-20mm GM/Bronze Ball Valve | As per relevaent standard specifications | 331 | EA | 331
295 | SWR34346 | 2 | S&F-25mm GM/Bronze Ball Valve | Civil work | S&F-25mm GM/Bronze Ball Valve | As per relevaent standard specifications | 466 | EA | 932
296 | SWR34329 | 4 | S&F-15mm Bib Tap 400gm Full turn | Civil work | S&F-15mm Bib Tap 400gm Full turn | As per relevaent standard specifications | 275 | EA | 1100
297 | SWR34375 | 500 | S&F Polyethylene Water Storage Tank | Civil work | S&F Polyethylene Water Storage Tank | As per relevaent standard specifications | 10 | L | 5000
298 | SWR33746 | 1 | Supply of Table 4'x2' with MS Frame | Civil work | Supply of Table 4'x2' with MS Frame | As per relevaent standard specifications | 4350 | EA | 4350
299 | SWR33857 | 1 | Supply of S-Type Chair | Civil work | Supply of S-Type Chair | As per relevaent standard specifications | 4035 | EA | 4035
300 | SWR33858 | 2 | Supply of PVC Chair | Civil work | Supply of PVC Chair | As per relevaent standard specifications | 1200 | EA | 2400
301 | SWR33422 | 2.5 | S&F Glow Sign Board | Civil work | S&F Glow Sign Board | As per relevaent standard specifications | 3735 | M2 | 9337.5
302 | SWR33421 | 1.35 | S&F MS Board | Civil work | S&F MS Board | As per relevaent standard specifications | 4545 | M2 | 6135.75
303 | SWR33415 | 7.3 | S&F RCC Hume Pipe of 450mm dia | Civil work | S&F RCC Hume Pipe of 450mm dia | As per relevaent standard specifications | 1345 | M | 9818.5
304 | SWR33406 | 165 | S&F RCC Fencing Pole 0.115mx0.115mx2.7m | Civil work | S&F RCC Fencing Pole 0.115mx0.115mx2.7m | As per relevaent standard specifications | 1443 | EA | 238095
305 | SWR33405 | 35 | S&F RCC Fencing Pole 0.1mx0.1mx1.8m | Civil work | S&F RCC Fencing Pole 0.1mx0.1mx1.8m | As per relevaent standard specifications | 1299 | EA | 45465
306 | SWR33407 | 300 | S&F Barbed Wire 8H & 2Cross | Civil work | S&F Barbed Wire 8H & 2Cross | As per relevaent standard specifications | 260 | M | 78000
307 | SWR33425 | 1 | Provd-Supply of Electricity to Site | Civil work | Provd-Supply of Electricity to Site | As per relevaent standard specifications | 5678 | EA | 5678
308 | SWR33608 | 1 | Geophysical Investgation Charges | Civil work | Geophysical Investgation Charges | As per relevaent standard specifications | 7000 | EA | 7000
309 | SWR33609 | 90 | Drilling-165mm Bore Well 0 to 90M | Civil work | Drilling-165mm Bore Well 0 to 90M | As per relevaent standard specifications | 336 | M | 30240
310 | SWR34830 | 30 | Drill-165mm Bore Well 90M to 120M | Civil work | Drill-165mm Bore Well 90M to 120M | As per relevaent standard specifications | 389 | M | 11670
311 | SWR34831 | 30 | Drill-165mm Bore Well 120M to 150M | Civil work | Drill-165mm Bore Well 120M to 150M | As per relevaent standard specifications | 407 | M | 12210
312 | SWR33611 | 30 | S&F 160mm dia PVC Casing | Civil work | S&F 160mm dia PVC Casing | As per relevaent standard specifications | 1650 | M | 49500
313 | SWR33636 | 1 | S&E SP SubMrsbl Pumpset 2.0HP 30 Stages | Civil work | S&E SP SubMrsbl Pumpset 2.0HP 30 Stages | As per relevaent standard specifications | 34894 | EA | 34894
314 | SWR33641 | 200 | S&R 3C 2.5sqmm Flat Copper Cable | Civil work | S&R 3C 2.5sqmm Flat Copper Cable | As per relevaent standard specifications | 210 | M | 42000
315 | SWR33644 | 1 | S&E D.O.L Starter 250V Single Phase | Civil work | S&E D.O.L Starter 250V Single Phase | As per relevaent standard specifications | 2400 | EA | 2400
316 | SWR34203 | 1 | Supply & fixing of Flange Clamps | Civil work | Supply & ixing of Flange Clamps | As per relevaent standard specifications | 191 | EA | 191
317 | SWR34410 | 178 | S&F-HDPE Pipe 40mm dia 16kg/sqcm-SDR 9 | Civil work | S&F-HDPE Pipe 40mm dia 16kg/sqcm-SDR 9 | As per relevaent standard specifications | 155 | M | 27590
318 | SWR34470 | 92.5 | Seigniorage Charges - Sand | Civil work | Seigniorage Charges - Sand | As per relevaent standard specifications | 40 | M3 | 3700
319 | SWR34471 | 80.1 | Seigniorage Charges - Metal | Civil work | Seigniorage Charges - Metal | As per relevaent standard specifications | 97.5 | M3 | 7809.75
320 | SWR34472 | 695 | Seigniorage Charges - Gravel | Civil work | Seigniorage Charges - Gravel | As per relevaent standard specifications | 30 | M3 | 20850
Total | [8 empty] | 7742682.6158
18% GST on Servicess | [8 empty] | 1393682.8708
Grand Total | [8 empty] | 9136365.4866