## DUPLICATE
Name of the Work:- Estimate for erection of 33/11KV sub-station, 33KV & 11KV lines at Badampet village in Kohir Mandal of Zaheerabad Division in Sangareddy circle Circle (WBS: S-1399-90-06-01-01-001).
SNO | SSR Code | Estimate Quantity (Only figures) | Item Detailed Specification Description | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item short Description
1 | SWR10105 | 39 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0')
2 | SWR10343 | 31 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole
3 | SWR10356 | 31.555 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.76x0.76x1.52M with CC mix of ratio 1:3:6 Using form boxes (0.88 Cu.Mt)*31 with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement
4 | SWR11890 | 0.961 | ERECTION OF S.S. STRUCTURE: Coping of 0.45x0.45x0.45Mt with 1:8 slope Using form boxes (0.031Cumt.) | Civil work | Coping & Muffing-Iron Pole
5 | SWR11331 | 31 | Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of poles with two coats of white cement (including cost of paint). | Electrical work | Paint-9.1M PSCC Poles as desc SSR
6 | SWR11889 | 5.5 | Fabrication of 100 X 50mm MS Channel for formation of 11kV and 33kV bays: Fabrication and erection of M.S,Channel 100x50mm for forming of 33KV & 11 KV Bays as per standard specifications to facilitate stringing of bus, erection of LA sets, AB Switches bolts & Nuts etc. including painting with one coats of red oxide and two coats of Aluminium paint. GI bolts&nuts shall be used. | Electrical work | Fabr & Erect-MS Chnl 100x50mm for SS Bay
7 | SWR10404 | 118.5 | Erection of 33kV and 11kV Strung Bus with Panther (200Sqmm) ACSR Conductor: Erection of 33kV and 11kV Bus over the Substation structures with 200sqmm Panther ACSR conductor and giving Jumpers to connect the Switch gear by providing the suitable T clamps and round clamps suitable to Post type insulators & Insulators. | Electrical work | Stringing of bus with panther conductor
8 | SWR10392 | 2 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 33kv ABSwitch incl earthing
9 | SWR10393 | 9 | Erection of 11kV AB Switches 800/400 Amps includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 11kv ABSwitch incl earthing
10 | SWR11742 | 3 | Supply & erection of 11 kV 400 A convential single(1/3) phasing AB switches.includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | S&E-400A 11KV ABSwth Conv 1ph(1/3) in SS
11 | SWR21240 | 2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt). | Electrical work | Hoisting post ins&hrd wr 1panther 33kv
12 | SWR21241 | 4 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Electrical work | Hoisting post ins&hrd wr 1panther 11kv
13 | SWR10881 | 11 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical work | Painting AB switch OP rods with PO red
14 | SWR23224 | 16.456 | Excavation of pit in all types of soils of size 2.2x2.2x0.85Mts.for Construction of Plinths for VCB (33KV & 11 KV ) | Earth work | Excavate-Pit for 33KV VCB
15 | SWR20685 | 22.264 | Providing of Base concreting (2.2x2.2x0.15 Mts) with 1:3:6 Concrete mix. Using form boxes, Providing of Concreting (2x2x1.0mts) with 1:3:6 Cocrete mix. Plastering of the plinth for smooth finishing with 12mm thick 1:3 cement motor and providing two coats white washing for part of the plinth above groung level. | Civil work | Cement concrete with 40MM metal VCB plin
16 | SWR10461 | 4 | Erection of Switchgear complete for 11 kV VCB includes Assembling the VCB Structures and mounting the VCBs over the already erected foudation including wiring of Breaker Control Panel/CTs, erection of CTs and control pannel providing Jumpers. | Electrical work | Erection of 11kv VCB
17 | SWR10396 | 2 | Erection of 33KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 33kv LA stn type incl earthing
18 | SWR10397 | 1 | Erection of 11 KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 11kv LA stn type incl earthing
19 | SWR10398 | 3 | Erection of 11 KV Lightening Arrestors line type complete including jumpering. | Electrical work | Erect of 11kvLA line type incl earthing
20 | SMR11607 | 1 | Supply of 33kv HG fuse set including providing of jumpers | Electrical work | S-33KV HG Fuse Set excl Ins & Chnl
21 | SWR10394 | 1 | Erection of 33kv HG fuse set including providing of jumpers | Electrical work | Erect. of 33kv HG Fuseset incl earthing
22 | SMR11608 | 1 | Supply of 11kv HG fuse set including providing of jumpers | Electrical work | S-11KV HG Fuse Set
23 | SWR10395 | 1 | Erection of 11kv HG fuse set including providing of jumpers | Electrical work | Erect. of 11kv HG Fuseset incl earthing
24 | SMR11482 | 23 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long
25 | SWR10357 | 23 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing
26 | SWR10920 | 500 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification.75x8 mm MS flat for Earth mat and connecting to electrodes. | Electrical work | Laying of earth mat,excavation 75x 8mm
27 | SWR10919 | 950 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification. 50x6 mm MS flat for raisers, double flat shall be run for structure poles raisers & equipment earthing. | Electrical work | Earthing for raisers of SS Flat 50x6 mm.
28 | SMR40033 | 2 | Providing of double earthing for neutral with flexible copper jumpers of adequate size including arrangement by fixing M.S.Channel 100x50mm. | Electrical work | SupCU Flexi jumper for Power T/F Neutral
29 | SWR11771 | 4 | Erection of 24 Volts Battery along with Charger on the VCB plinth and giving DC supply to VCB's. | Electrical work | Erect-24V Batery with Chrgr incl grot-SS
30 | SWR11474 | 700 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable includes excavation of earth and back filling with sand and earth in alternate layers . The cable termination shall be made by providing proper size lugs and shall be identified with colours. | Electrical work | Laying-4 core cable
31 | SWR10463 | 1 | Erection of 25 KVA Three phase Station Transformer on the Substation Structures and giving jumpers/connections on HT side to the 11kV bus. Belting angle shall be provided both sides of DTR for securing DTR firmly in position. | Electrical work | Erection of Three Phase DTRs
32 | SMR40045 | 1 | Supply of AC Panel Board includes: Fixing of 1 No.100A, MCCB, 10kA capacity of any standard make including material cost. Fixing of suitable panel box 3x3x1 with M.S.Sheet of 16 SWG with front door compartments inclusive of material cost & powder coating (with C Channel ). Fabrication of panel Fixing of 96x96mm analog voltmeter with VSS switch Fixing of 20A HRC fuse Fixing of 3 phase supply indicator kwith HRC fuses Supply and fixing of 6 Sqmm copper flexible wire (PVC) Fixing of Stud type TBs for outgoing feeder Fixing of Epoxy bus supports. | Electrical work | Supply of AC Supply panel complete
33 | SMR40044 | 1 | Supply of DC Panel Board Fixing of suitable panel box of size 6'x6'x1' with M S sheet of 16 SWG with back doors (4'x6') and on front side with provision to fix up bakelite hylam sheet size of 4'x6' including cost of the panel with powder coating. Fixing of best quality of angles for panel. Fixing of C Channelfor panel. Fabrication of control panel including making suitable holes and board Fixing of Stud type TBs for outgoing feeder Fixing of 24V DC pilot lamps of standard make Fixing of healthy trip push buttons with LED lamp Fixing of plain switches for alarm acceptance and for PTR signal Fixing of ON/OFF push buttons Fixing of digital volt meter for 11kV Fixing of VSS of standard make, Fixing of Engraved AL plates for Alarm panel of various VCB Laying of 2.5Sqmm copper flexible wire for internal wiring . Fixing of digital frequency meter Fixing of Copper lugs and ferrules for internal wiring. Fixing of 4" Gang bells 24V DC Fixing of flow diagram with rading strip Fixing of HRC fuse units | Electrical work | Supply of DC Anunc.relay panel 8 feeders
34 | SWR20025 | 1 | fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supplied by tenderer. | Electrical work | Erect-Contrl/Relay, AC, Announ. Panels
35 | SWR10342 | 8 | Erection of 8.0 Mts PSCC Poles complete with necessary hard ware for yard lighting excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole
36 | SWR10956 | 8 | Fixing of Metal halide/LED lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5M GI pipe complete. | Electrical work | Fixing of LED/Metal halide complete.
37 | SWR20028 | 8 | Supply and Fixing of junction box and Providing with proper Fuse protection and required glauds suitable for Cable Terminations. The box shall be fixed on the pole. | Electrical work | 33/11kv S.S Yard lighting junction box
38 | SWR20526 | 2 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply & fixing of marshall box
39 | SMR40088 | 1 | Supply and fixing of filled sand bucket set complete (4 Nos. Buckets) with stand to mount fire buckets. | Electrical work | Sup Fire Buckets Stand with Buckets
40 | SMR40087 | 2 | Supply and fixing of CO2 Cylinder set as per IS2878 Specifications. | Electrical work | Sup TrollyMounted Co2 Cylinders(IS-2878)
41 | SWR11895 | 1 | Supplying and fixing of feeder indicator board to each of the 3Nos feeder breakers and LV breaker, danger boards made of 1'x1' and properly mounted on the structures. The letters written on the borad shall be 1.5"size with blue colour and background shall be of white colour | Electrical work | S&F-33/11KV SS Feeder Indicator Board
42 | SWR20032 | 1 | Supply and fixing of wooden board of size 3'x2'.5'indicating the layout of the Switch yard. | Electrical work | Sup &fix of board ind Switchyard layout
43 | SMR40086 | 1 | Supply and Erection of Permanent Name Board of on 3'x4' steel sheetmounted on steel frame as described in Specification. | Electrical work | Sup 33/11kv S.S Permanent name board
44 | SMR40076 | 1 | Supply of Digital clamp meter. | Electrical work | Supply of Digital clamp meter.
45 | SMR40064 | 1 | Supply of Rechargeable LED torch light of Standard make. | Electrical work | Sup Rechargeable LED torch light.
46 | SMR40063 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box containing ‘D’Spanners from size 6 to 54, Hammer small and big size, Ring spanners from 6 to 28, Adjustable spanner, Pipe wrench, Cutting Plier, Nose plier, Tester, insulated Screw drive. | Electrical work | SupTaparia Tool kit complete as per Spec
47 | SWR22090 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Electrical work | Sup& fix safety inst/SS Op. inst board
48 | SMR11598 | 8 | Supply of 25 W LED lamp with fitting of philips make | Electrical work | S-25W LED fixture set
49 | SMR12378 | 1 | Supply of Alluminum Ladder(20 feet) | Electrical work | S-10ft Aluminium Ladder
50 | SMR40075 | 1 | Supply of Megger (2000 ohms, 0-2.5kv) | Electrical work | Supply of Earth megger (1000v)
51 | SMR11599 | 4 | Supply of Earth Discharging Rod 10' length. | Electrical work | S-Earth Rod 8ft Long 3mm Thick
52 | SMR11488 | 250 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc.,
53 | SMR11591 | 66 | Supply of PG clamps for panther 2 bolted 800 A. | Electrical work | S-Al. alloy three bolted PG clamps 800A
54 | SWR20029 | 200 | Supply and Laying of 2 core/4 core cable includes excavation earth and back filling with sand and earth in alternate layers as shown in the sketch. The cable termination shall be made by providing proper size of lugs at both ends of the cable termination. | Electrical work | 33/11kv S.S laying of 2/4core for light
55 | SWR20308 | 31 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM
56 | SWR20307 | 8 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM
57 | SWR11860 | 2 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip. | Electrical work | Transport of Cond Drum,VCBs upto 10Km
58 | SWR10150 | 10.61 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM
59 | SWR10206 | 10.61 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods
60 | SWR10524 | 10.61 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod
61 | SWR11220 | 354 | Loading and unwinding of Panther conductor. | Electrical work | Load-Unwinding Panther conductor
62 | SWR11221 | 354 | Unloading of Panther conductor. | Electrical work | Unload-Unwinding Panther conductor
63 | SWR12416 | 2 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators
64 | SWR10631 | 2 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator
65 | SWR10618 | 2 | Loading of 33KV Metal parts bag of 25 nos. | Electrical work | LOADING of 33KV Metal parts-bag of 25no
66 | SWR10632 | 2 | Unloading of 33 KV Metal parts bag of 25 nos. | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25
67 | SWR10212 | 2 | Loading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | LOADING of 11kv Pin/Post/Solid Core Insu
68 | SWR10530 | 2 | Unloading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | UNLOADING of 11kv Pin/Post/Solid Core In
69 | SWR11701 | 700 | Loading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | Load-PVC Control Cable 10C
70 | SWR11712 | 700 | Unloading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | UnLoad-PVC Control Cable 10C
71 | SWR11691 | 1 | Loading of 3Ph 25KVA Distribution Transformer. | Electrical work | Load-3Ph 25KVA DTR
72 | SWR11692 | 1 | UnLoading of 3Ph 25KVA Distribution Transformer. | Electrical work | UnLoad-3Ph 25KVA DTR
73 | SWR10200 | 1 | Loading of 33/11 KV Current Transformers/ Potential Transformers. | Electrical work | LOADING of 33/11 KV CTs/ PTs
74 | SWR10266 | 3 | Loading of 33 KV10 KA LAs Station type. | Electrical work | LOADING of 33 KV10 KA LAs Station type
75 | SWR10584 | 3 | Unloading of 33 KV10 KA LAs Station type. | Electrical work | UNLOADING of 33 KV10 KA LAs Station type
76 | SWR10265 | 9 | Loading of 11 KV10 KA LAs Line type. | Electrical work | LOADING of 11 KV, 10 KA LAs Line type
77 | SWR10583 | 9 | Unloading of 11 KV10 KA LAs Line type. | Electrical work | UNLOADING of 11 KV, 10 KA LAs Line type
78 | SWR10264 | 3 | Loading of 11 KV10 KA LAs Station type. | Electrical work | LOADING of 11 KV,10 KA LAs Station type
79 | SWR10582 | 3 | Unloading of 11 KV10 KA LAs Station type. | Electrical work | UNLOADING of 11 KV,10 KA LAs Station typ
80 | SWR10239 | 2 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A
81 | SWR10557 | 2 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A
82 | SWR10238 | 9 | loading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | LOADING of 11 KV AB SWCH Con 200/400 A
83 | SWR10556 | 9 | Unloading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A
84 | SWR11224 | 4 | Loading and Unloading of 12V/24V Battery Set. | Electrical work | Load/Unload-12V/24V Battery Set
85 | SWR10402 | 1 | Erection of 11kv Potential Transformer sets complete including jumpering. The LV side of the PT shall be provided with proper fuse protection mounted in separate marshalling boxwith proper size cable glands etc. The box shall be mounted on the Substation structure. | Electrical work | Erection of 11kv three phase PT s
86 | SWR10518 | 1 | Unloading of 33/11 KV Current Transformers/ Potential Transformers | Electrical work | UNLOADING of 33/11 KV CTs/ PTs
87 | SWR10674 | 1 | Fixing of Distribution Box and Providing with proper Fuse protection system and reqired Cable Terminations at Station T/F LT side and AC/DC Panel and fixing meter. Power cable of adequate size shall be provided from station DTR to control room AC Panel. | Electrical work | Erection of LT distribution box
88 | SWR21750 | 1 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply and fixing of PT Marshalling box
89 | SMR40067 | 2 | Supply of Hand Gloves | Electrical work | Supply of Hand Gloves
90 | SMR40071 | 2 | Supply of Safety Helmets of standard make | Electrical work | Supply of Safety Helmet of standard make
91 | SMR40009 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for First coat of 1st GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 1st coat Al. Painting.
92 | SWR10877 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 1st coat of Aluminium | Electrical work | Labour for 1st coat Al. Painting.
93 | SWR20904 | 20 | Supply & Providing of Panther T clamps. | Electrical work | Supply & Providing of Panther T clamps.
94 | SMR40010 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for second coat of 2nd GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 2nd coat Al. Painting.
95 | SWR10879 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 2nd coat of Aluminium | Electrical work | Labour for 2nd coat Al. Painting.
96 | SWR10110 | 4 | Excavation of Pole pits of size (2.6" x 2.6" x 5.0') 0.88 cum 0.76 M x 0.76M x 1.52M for 9.1 mtrs PSCC Poles including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAV. OF PIT HARD(2.6" x 2.6" x 5.0")
97 | SWR10105 | 4 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0')
98 | SWR10978 | 4 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole
99 | SWR10343 | 4 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole
100 | SWR10356 | 8.008 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.76x0.76x1.52M with CC mix of ratio 1:3:6 Using form boxes (0.88 Cu.Mt)*31 with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement
101 | SWR10868 | 0.7 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the ply and fabrication of 6mm base and top plate for Box pole to theRS Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | Electrical work | Fabriction of structure
102 | SWR10404 | 5 | Erection of 33kV and 11kV Strung Bus with Panther (200Sqmm) ACSR Conductor: Erection of 33kV and 11kV Bus over the Substation structures with 200sqmm Panther ACSR conductor and giving Jumpers to connect the Switch gear by providing the suitable T clamps and round clamps suitable to Post type insulators & Insulators. | Electrical work | Stringing of bus with panther conductor
103 | SWR10392 | 2 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 33kv ABSwitch incl earthing
104 | SWR10396 | 1 | Erection of 33KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 33kv LA stn type incl earthing
105 | SMR11482 | 4 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long
106 | SWR10357 | 4 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing
107 | SMR11488 | 25 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc.,
108 | SMR40036 | 12 | Sup PG clamps for panther 2 bolted 600 A | Electrical work | Sup PG clamps for panther 2 bolted 600 A
109 | SWR10239 | 2 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A
110 | SWR10557 | 2 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A
111 | SWR10150 | 0.89 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM
112 | SWR10206 | 0.89 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods
114 | SWR10263 | 4 | LOADING of CI Earth pipe upto 2.7 Mtr | Electrical work | LOADING of CI Earth pipe upto 2.7 Mtr
115 | SWR10581 | 4 | UNLOADING of CI Earth pipe upto 2.7 Mtr | Electrical work | UNLOADING of CI Earth pipe upto 2.7 Mtr
116 | SWR22092 | 8.85 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 33 kv line | Earth work | survey line&cabl inc peg mark&tree clear | 33kv line
117 | SWR10108 | 15 | Excavation of Pole pits of size 0.76x0.9x1.95 Mts' for 12.5 mts spun Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | Excavation of pit
118 | SWR10107 | 103 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0")
119 | SWR10112 | 60 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0")
120 | SWR10105 | 39 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0')
121 | SWR21933 | 95 | Excavation of Stay pits of size 0.45x0.45x1.265 Mts' for burying the anchor rod with anchor plate of stay sets including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits any and leveling the site with out any lead.In all soils with Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting.. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr
122 | SWR10350 | 15 | Erection of 12.5 Mtr spun pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 12.5 M long spun pole
123 | SWR10319 | 15 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 75 x 8 mm MS Flat | Electrical work | Fab Back clamps with 75 x 8 mm MS Flat
124 | SWR10978 | 163 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole
125 | SWR10343 | 39 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole
126 | SWR10981 | 36 | Formation of 33 kv cut points (Vertical/Horizantal) including fixing of Clamps and top cleat and fixing of pin insulator complete with necessary hard wear for stud locations excluding the cost of pit Excavation and the pole shall be numbered with colour paint and earthing. | Electrical work | Horizontal Cut point for 33 KV line
127 | SWR10356 | 67.97 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.76x0.76x1.52M with CC mix of ratio 1:3:6 Using form boxes (0.88 Cu.Mt)*31 with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement
128 | SWR10366 | 8.85 | Paving of the 100 sqmm AAA conductor and stringing duly arranging temporary guys, tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pin binding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing 100sqmm 33/11kv Line 3 Cond SC
129 | SMR11488 | 220 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc.,
131 | SWR11180 | 163 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM
132 | SWR20308 | 39 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM
133 | SWR10191 | 6 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums
134 | SWR10509 | 6 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums
135 | SWR11860 | 6 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip. | Electrical work | Transport of Cond Drum,VCBs upto 10Km
136 | SWR10150 | 1.985 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM
137 | SWR10206 | 1.985 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods
138 | SWR10524 | 1.985 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod
139 | SWR10211 | 87 | Loading of 33 KV Pin insulators | Electrical work | LOADING of 33 KV Pin insulators
140 | SWR10529 | 87 | Unloading of 33 KV Pin insulators | Electrical work | UNLOADING of 33 KV Pin insulators
141 | SWR12416 | 36 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators
142 | SWR10631 | 36 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator
143 | SWR10618 | 36 | Loading of 33KV Metal parts bag of 25 nos. | Electrical work | LOADING of 33KV Metal parts-bag of 25no
144 | SWR10632 | 36 | Unloading of 33 KV Metal parts bag of 25 nos. | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25
145 | SWR10354 | 95 | Erection of 33 kv Stay set complete including fixing of bow ,fixing and binding of Eye bolt, Anchor rod, guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. | Electrical work | Assembly and erection of Stay set 33kv
146 | SWR20819 | 34.304 | Mass concreting of STAY LOCATIONS | Civil work | Mass concreting of stays incl. cement
147 | SWR10392 | 2 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 33kv ABSwitch incl earthing
148 | SWR10105 | 8 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0')
149 | SWR10107 | 4 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0")
151 | SWR10343 | 8 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole
152 | SWR10978 | 4 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole
153 | SWR10356 | 7.88 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.76x0.76x1.52M with CC mix of ratio 1:3:6 Using form boxes (0.88 Cu.Mt)*31 with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement
154 | SMR11488 | 10 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc.,
155 | SWR10206 | 0.68 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods
156 | SWR10524 | 0.68 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod
157 | SWR10134 | 0.68 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM
159 | SWR20308 | 8 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM
160 | SWR11180 | 4 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM
161 | SWR12402 | 1 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts
162 | SWR12421 | 1 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag
163 | SWR12416 | 1 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators
164 | SWR10631 | 1 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator
165 | SMR11482 | 4 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long
166 | SWR10357 | 4 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing
167 | SMR11485 | 64 | Supply of earthing GI Flat 25X3 mm including material | Electrical work | S-Earthing GI flat 25x3 mm incl material
168 | SWR10239 | 2 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A
169 | SWR10557 | 2 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A
170 | SWR22092 | 3.36 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 33 kv line | Earth work | survey line&cabl inc peg mark&tree clear | 11kv line
171 | SWR10108 | 21 | Excavation of Pole pits of size 0.76x0.9x1.95 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting | Earth work | EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0")
172 | SWR10105 | 11 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0')
173 | SWR10107 | 30 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0")
174 | SWR21933 | 32 | Excavation of Stay pits of size 0.45x0.45x1.265 Mts' for burying the anchor rod with anchor plate of stay sets including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits any and leveling the site with out any lead.In all soils with Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting | Earth work | Excavation of stay pit size 0.45x0.45x1.265 mts with hard soil
175 | SWR10978 | 21 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole
176 | SWR10342 | 11 | Erection of 8.0 Mts PSCC Poles complete with necessary hard ware for yard lighting excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole
177 | SWR10343 | 30 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole
178 | SWR10653 | 17 | Formation of 11 kv cut points (Vertical/Horizantal) including fixing of 11 KV Cross arms,clamps, strain insulators sets complete with hardware and stays (Bows and Eye-bolts), Excluding the cost of pit Excavation and pole erection. The contractor has to supply GI Bolts and Nuts. | Electrical work | Formatn of Horiz Cut point for 11KV line
179 | SWR10356 | 8.008 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.76x0.76x1.52M with CC mix of ratio 1:3:6 Using form boxes (0.88 Cu.Mt)*31 with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement
180 | SWR10356 | 13.312 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.76x0.76x1.52M with CC mix of ratio 1:3:6 Using form boxes (0.88 Cu.Mt)*31 with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement
181 | SWR10365 | 1.01 | Paving of the conductor 55 Sqmm Single Circuit (3 Conductors) AAAC and stringing duly arranging temporary guys,tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pinbinding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing of 55sqmm 33/11kv Line 3 Cond
182 | SWR10703 | 1.05 | Paving of the conductor 55 Sqmm double Circuit (6 Conductors) AAAC and stringing duly arranging temporary guys,tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pinbinding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing of 55sqmm 33/11kv Line 6 Cond
183 | SMR11488 | 150 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc.,
184 | SWR10206 | 1.271 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods
185 | SWR10524 | 1.271 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod
186 | SWR11248 | 185 | Loading 11KV Polymer Pin Insulator with GI pins | Electrical work | Load-11KV Polymer Pin Insulator-GI pin
187 | SWR11249 | 185 | Unloading 11KV Polymer Pin Insulator with GI pins | Electrical work | Unload-11KV Polymer Pin Insulator-GI pin
188 | SWR10134 | 1.271 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM
189 | SWR11862 | 2 | Transport of VCB , Control pannels, current transformater, bosster etc, above 20 KM and upto 30 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs >20 & <30Km
190 | SWR10191 | 2 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums
191 | SWR10509 | 2 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums
192 | SWR20307 | 11 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM
193 | SWR20308 | 30 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM
194 | SWR11180 | 21 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM
195 | SWR10228 | 34 | Loading of 11 KV V - Cross arms | Electrical work | LOADING of 11 KV V - Cross arms
196 | SWR10546 | 34 | Unloading of 11 KV V - Cross arms | Electrical work | UNLOADING of 11 KV V - Cross arms
197 | SWR12402 | 10 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts
198 | SWR12421 | 10 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag
199 | SWR10251 | 16 | Loading of 11 KV Top fittings | Electrical work | LOADING of 11 KV Top fittings
200 | SWR10569 | 16 | Unloading of 11 KV Top fittings | Electrical work | UNLOADING of 11 KV Top fittings
201 | SWR12416 | 10 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators
202 | SWR10631 | 10 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator
203 | SWR10353 | 32 | Erection of 11 kv Stay set complete including fixing of bow, fixing and binding of Eye bolt,Anchor rod,guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Assembly and erection of Stay set11kv&LT
204 | SWR10393 | 4 | Erection of 11kV AB Switches 800/400 Amps includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 11kv ABSwitch incl earthing
205 | SMR11488 | 8 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc.,
206 | SWR10206 | 0.274 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods
207 | SWR10524 | 0.274 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod
208 | SWR10134 | 0.274 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM
209 | SMR11484 | 4 | Supply of C I earth pipe of size 50mm dia, 2 mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 50mm dia 2m long
210 | SWR11222 | 8 | Loading/Unloading of C I earth pipe of size 80/50mm dia, 2 mtrs long for earth electrode | Electrical work | Load/Unload-CI pipe 80/50 mm dia 2mt L
211 | SWR34671 | 4 | Providing of collar rings of 450mm dia at 4 pole structure | Electrical work | Collar/ Rings of 450mm dia
212 | SMR11485 | 40 | Supply of earthing GI Flat 25X3 mm including material | Electrical work | S-Earthing GI flat 25x3 mm incl material
213 | SWR10238 | 4 | loading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | LOADING of 11 KV AB SWCH Con 200/400 A
214 | SWR10556 | 4 | Unloading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A
4207471

## Badampet FINAL
Schedule(WBS: S-1399-90-06-01-01-001 & S-1399-90-07-01-01-001 )
Name of the Work:- Erection of 33/11KV sub-stationalong with connected 33KV & 11KV lines along with Construction of control room at Badampet village in Kohir Mandal of Zaheerabad Division in Sangareddy circle
S.No | SSR Code | Estimate Quantity (Only figures) | Item Detailed Specification Description | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SWR10105 | 39 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 23400
2 | SWR10343 | 31 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 74400
3 | SWR10356 | 31.555 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.76x0.76x1.52M for 9.1mts poles and 0.6x0.6x 1.5 for 8 mts bpoles with CC mix of ratio 1:3:6 Using form boxes (0.88 Cu.Mt)*31 and (0.546 cu.mt)*8 with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 207600.345
4 | SWR11890 | 0.961 | ERECTION OF S.S. STRUCTURE: Coping of 0.45x0.45x0.45Mt with 1:8 slope Using form boxes (0.031Cumt.) | Civil work | Coping & Muffing-Iron Pole | As per relevent standard specification | 3893 | M3 | 3741.173
5 | SWR11331 | 31 | Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of poles with two coats of white cement (including cost of paint). | Electrical work | Paint-9.1M PSCC Poles as desc SSR | As per relevent standard specification | 485 | EA | 15035
6 | SWR11889 | 5.5 | Fabrication of 100 X 50mm MS Channel for formation of 11kV and 33kV bays: Fabrication and erection of M.S,Channel 100x50mm for forming of 33KV & 11 KV Bays as per standard specifications to facilitate stringing of bus, erection of LA sets, AB Switches bolts & Nuts etc. including painting with one coats of red oxide and two coats of Aluminium paint. GI bolts&nuts shall be used. | Electrical work | Fabr & Erect-MS Chnl 100x50mm for SS Bay | As per relevent standard specification | 6600 | TO | 36300
7 | SWR10404 | 118.5 | Erection of 33kV and 11kV Strung Bus with Panther (200Sqmm) ACSR Conductor: Erection of 33kV and 11kV Bus over the Substation structures with 200sqmm Panther ACSR conductor and giving Jumpers to connect the Switch gear by providing the suitable T clamps and round clamps suitable to Post type insulators & Insulators. | Electrical work | Stringing of bus with panther conductor | As per relevent standard specification | 327.68 | M | 38830.08
8 | SWR10392 | 2 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 9000
9 | SWR10393 | 9 | Erection of 11kV AB Switches 800/400 Amps includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 28800
10 | SWR11742 | 3 | Supply & erection of 11 kV 400 A convential single(1/3) phasing AB switches.includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | S&E-400A 11KV ABSwth Conv 1ph(1/3) in SS | As per relevent standard specification | 4232 | EA | 12696
11 | SWR21240 | 2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt). | Electrical work | Hoisting post ins&hrd wr 1panther 33kv | As per relevent standard specification | 781 | EA | 1562
12 | SWR21241 | 4 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Electrical work | Hoisting post ins&hrd wr 1panther 11kv | As per relevent standard specification | 507 | EA | 2028
13 | SWR10881 | 11 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 1562
14 | SWR23224 | 16.46 | Excavation of pit in all types of soils of size 2.2x2.2x0.85Mts.for Construction of Plinths for VCB (33KV & 11 KV ) | Earth work | Excavate-Pit for 33KV VCB | As per relevent standard specification | 331 | M3 | 5448.26
15 | SWR20685 | 22.264 | Providing of Base concreting (2.2x2.2x0.15 Mts) with 1:3:6 Concrete mix. Using form boxes, Providing of Concreting (2x2x1.0mts) with 1:3:6 Cocrete mix. Plastering of the plinth for smooth finishing with 12mm thick 1:3 cement motor and providing two coats white washing for part of the plinth above groung level. | Civil work | Cement concrete with 40MM metal VCB plin | As per relevent standard specification | 5160 | M3 | 114882.24
16 | SWR10461 | 4 | Erection of Switchgear complete for 11 kV VCB includes Assembling the VCB Structures and mounting the VCBs over the already erected foudation including wiring of Breaker Control Panel/CTs, erection of CTs and control pannel providing Jumpers. | Electrical work | Erection of 11kv VCB | As per relevent standard specification | 12000 | EA | 48000
17 | SWR10396 | 2 | Erection of 33KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 33kv LA stn type incl earthing | As per relevent standard specification | 880 | SET | 1760
18 | SWR10397 | 1 | Erection of 11 KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 11kv LA stn type incl earthing | As per relevent standard specification | 559 | SET | 559
19 | SWR10398 | 3 | Erection of 11 KV Lightening Arrestors line type complete including jumpering. | Electrical work | Erect of 11kvLA line type incl earthing | As per relevent standard specification | 505 | SET | 1515
20 | SMR11607 | 1 | Supply of 33kv HG fuse set including providing of jumpers | Electrical work | S-33KV HG Fuse Set excl Ins & Chnl | As per relevent standard specification | 6431 | SET | 6431
21 | SWR10394 | 1 | Erection of 33kv HG fuse set including providing of jumpers | Electrical work | Erect. of 33kv HG Fuseset incl earthing | As per relevent standard specification | 1331.81 | SET | 1331.81
22 | SMR11608 | 1 | Supply of 11kv HG fuse set including providing of jumpers | Electrical work | S-11KV HG Fuse Set | As per relevent standard specification | 1733.75 | SET | 1733.75
23 | SWR10395 | 1 | Erection of 11kv HG fuse set including providing of jumpers | Electrical work | Erect. of 11kv HG Fuseset incl earthing | As per relevent standard specification | 740.52 | SET | 740.52
24 | SMR11482 | 23 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 80178
25 | SWR10357 | 23 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 28386.6
26 | SWR10920 | 500 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification.75x8 mm MS flat for Earth mat and connecting to electrodes. | Electrical work | Laying of earth mat,excavation 75x 8mm | As per relevent standard specification | 65 | RMT | 32500
27 | SWR10919 | 950 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification. 50x6 mm MS flat for raisers, double flat shall be run for structure poles raisers & equipment earthing. | Electrical work | Earthing for raisers of SS Flat 50x6 mm. | As per relevent standard specification | 41 | RMT | 38950
28 | SMR40033 | 2 | Providing of double earthing for neutral with flexible copper jumpers of adequate size including arrangement by fixing M.S.Channel 100x50mm. | Electrical work | SupCU Flexi jumper for Power T/F Neutral | As per relevent standard specification | 4725 | EA | 9450
29 | SWR11771 | 4 | Erection of 24 Volts Battery along with Charger on the VCB plinth and giving DC supply to VCB's. | Electrical work | Erect-24V Batery with Chrgr incl grot-SS | As per relevent standard specification | 1050 | EA | 4200
30 | SWR11474 | 700 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable includes excavation of earth and back filling with sand and earth in alternate layers . The cable termination shall be made by providing proper size lugs and shall be identified with colours. | Electrical work | Laying-4 core cable | As per relevent standard specification | 15 | RMT | 10500
31 | SWR10463 | 1 | Erection of 25 KVA Three phase Station Transformer on the Substation Structures and giving jumpers/connections on HT side to the 11kV bus. Belting angle shall be provided both sides of DTR for securing DTR firmly in position. | Electrical work | Erection of Three Phase DTRs | As per relevent standard specification | 1139.95 | EA | 1139.95
32 | SMR40045 | 1 | Supply of AC Panel Board includes: Fixing of 1 No.100A, MCCB, 10kA capacity of any standard make including material cost. Fixing of suitable panel box 3x3x1 with M.S.Sheet of 16 SWG with front door compartments inclusive of material cost & powder coating (with C Channel ). Fabrication of panel Fixing of 96x96mm analog voltmeter with VSS switch Fixing of 20A HRC fuse Fixing of 3 phase supply indicator kwith HRC fuses Supply and fixing of 6 Sqmm copper flexible wire (PVC) Fixing of Stud type TBs for outgoing feeder Fixing of Epoxy bus supports. | Electrical work | Supply of AC Supply panel complete | As per relevent standard specification | 42000 | EA | 42000
33 | SMR40044 | 1 | Supply of DC Panel Board Fixing of suitable panel box of size 6'x6'x1' with M S sheet of 16 SWG with back doors (4'x6') and on front side with provision to fix up bakelite hylam sheet size of 4'x6' including cost of the panel with powder coating. Fixing of best quality of angles for panel. Fixing of C Channelfor panel. Fabrication of control panel including making suitable holes and board Fixing of Stud type TBs for outgoing feeder Fixing of 24V DC pilot lamps of standard make Fixing of healthy trip push buttons with LED lamp Fixing of plain switches for alarm acceptance and for PTR signal Fixing of ON/OFF push buttons Fixing of digital volt meter for 11kV Fixing of VSS of standard make, Fixing of Engraved AL plates for Alarm panel of various VCB Laying of 2.5Sqmm copper flexible wire for internal wiring . Fixing of digital frequency meter Fixing of Copper lugs and ferrules for internal wiring. Fixing of 4" Gang bells 24V DC Fixing of flow diagram with rading strip Fixing of HRC fuse units | Electrical work | Supply of DC Anunc.relay panel 8 feeders | As per relevent standard specification | 42500 | EA | 42500
34 | SWR20025 | 1 | fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supplied by tenderer. | Electrical work | 33/11kv S.S Erection of AC&DC Panel | As per relevent standard specification | 7871.85 | SET | 7871.85
35 | SWR10342 | 8 | Erection of 8.0 Mts PSCC Poles complete with necessary hard ware for yard lighting excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 12000
36 | SWR10956 | 8 | Fixing of Metal halide/LED lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5M GI pipe complete. | Electrical work | Fixing of LED/Metal halide complete. | As per relevent standard specification | 1268 | EA | 10144
37 | SWR20028 | 8 | Supply and Fixing of junction box and Providing with proper Fuse protection and required glauds suitable for Cable Terminations. The box shall be fixed on the pole. | Electrical work | 33/11kv S.S Yard lighting junction box | As per relevent standard specification | 351.9 | EA | 2815.2
38 | SWR20526 | 2 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply & fixing of marshall box | As per relevent standard specification | 3085.5 | EA | 6171
39 | SMR40088 | 1 | Supply and fixing of filled sand bucket set complete (4 Nos. Buckets) with stand to mount fire buckets. | Electrical work | Sup Fire Buckets Stand with Buckets | As per relevent standard specification | 1386 | SET | 1386
40 | SMR40087 | 2 | Supply and fixing of CO2 Cylinder set as per IS2878 Specifications. | Electrical work | Sup TrollyMounted Co2 Cylinders(IS-2878) | As per relevent standard specification | 9240 | EA | 18480
41 | SWR11895 | 1 | Supplying and fixing of feeder indicator board to each of the 3Nos feeder breakers and LV breaker, danger boards made of 1'x1' and properly mounted on the structures. The letters written on the borad shall be 1.5"size with blue colour and background shall be of white colour | Electrical work | S&F-33/11KV SS Feeder Indicator Board | As per relevent standard specification | 551 | SET | 551
42 | SWR20032 | 1 | Supply and fixing of wooden board of size 3'x2'.5'indicating the layout of the Switch yard. | Electrical work | Sup &fix of board ind Switchyard layout | As per relevent standard specification | 1654 | EA | 1654
43 | SMR40086 | 1 | Supply and Erection of Permanent Name Board of on 3'x4' steel sheetmounted on steel frame as described in Specification. | Electrical work | Sup 33/11kv S.S Permanent name board | As per relevent standard specification | 10238 | EA | 10238
44 | SMR40076 | 1 | Supply of Digital clamp meter. | Electrical work | Supply of Digital clamp meter. | As per relevent standard specification | 2888 | EA | 2888
45 | SMR40064 | 1 | Supply of Rechargeable LED torch light of Standard make. | Electrical work | Sup Rechargeable LED torch light. | As per relevent standard specification | 1733 | EA | 1733
46 | SMR40063 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box containing ‘D’Spanners from size 6 to 54, Hammer small and big size, Ring spanners from 6 to 28, Adjustable spanner, Pipe wrench, Cutting Plier, Nose plier, Tester, insulated Screw drive. | Electrical work | SupTaparia Tool kit complete as per Spec | As per relevent standard specification | 4925 | SET | 4925
47 | SWR22090 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Electrical work | Sup& fix safety inst/SS Op. inst board | As per relevent standard specification | 2205 | EA | 2205
48 | SMR11598 | 8 | Supply of 25 W LED lamp with fitting of philips make | Electrical work | S-25W LED fixture set | As per relevent standard specification | 3200 | EA | 25600
49 | SMR12378 | 1 | Supply of Alluminum Ladder(20 feet) | Electrical work | S-10ft Aluminium Ladder | As per relevent standard specification | 1654 | EA | 1654
50 | SMR40075 | 1 | Supply of Megger (2000 ohms, 0-2.5kv) | Electrical work | Supply of Earth megger (1000v) | As per relevent standard specification | 8085 | EA | 8085
51 | SMR11599 | 4 | Supply of Earth Discharging Rod 10' length. | Electrical work | S-Earth Rod 8ft Long 3mm Thick | As per relevent standard specification | 1000 | EA | 4000
52 | SMR11488 | 250 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 29375
53 | SMR11591 | 66 | Supply of PG clamps for panther 2 bolted 800 A. | Electrical work | S-Al. alloy three bolted PG clamps 800A | As per relevent standard specification | 130 | EA | 8580
54 | SWR20029 | 200 | Supply and Laying of 2 core/4 core cable includes excavation earth and back filling with sand and earth in alternate layers as shown in the sketch. The cable termination shall be made by providing proper size of lugs at both ends of the cable termination. | Electrical work | 33/11kv S.S laying of 2/4core for light | As per relevent standard specification | 50 | M | 10000
55 | SWR20308 | 31 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 12625.99
56 | SWR20307 | 8 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 2172.16
57 | SWR11860 | 2 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip. | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 5440.68
58 | SWR10150 | 10.61 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 6547.431
59 | SWR10206 | 10.61 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 2344.81
60 | SWR10524 | 10.61 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 1962.85
61 | SWR11220 | 354 | Loading and unwinding of Panther conductor. | Electrical work | Load-Unwinding Panther conductor | As per relevent standard specification | 3 | M | 1062
62 | SWR11221 | 354 | Unloading of Panther conductor. | Electrical work | Unload-Unwinding Panther conductor | As per relevent standard specification | 2 | M | 708
63 | SWR12416 | 2 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | KI | 4
64 | SWR10631 | 2 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | KI | 4
65 | SWR10618 | 2 | Loading of 33KV Metal parts bag of 25 nos. | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 130
66 | SWR10632 | 2 | Unloading of 33 KV Metal parts bag of 25 nos. | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 130
67 | SWR10212 | 2 | Loading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | LOADING of 11kv Pin/Post/Solid Core Insu | As per relevent standard specification | 1 | KI | 2
68 | SWR10530 | 2 | Unloading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | UNLOADING of 11kv Pin/Post/Solid Core In | As per relevent standard specification | 1 | KI | 2
69 | SWR11701 | 700 | Loading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | Load-PVC Control Cable 10C | As per relevent standard specification | 1 | M | 700
70 | SWR11712 | 700 | Unloading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | UnLoad-PVC Control Cable 10C | As per relevent standard specification | 1.02 | M | 714
71 | SWR11691 | 1 | Loading of 3Ph 25KVA Distribution Transformer. | Electrical work | Load-3Ph 25KVA DTR | As per relevent standard specification | 252 | EA | 252
72 | SWR11692 | 1 | UnLoading of 3Ph 25KVA Distribution Transformer. | Electrical work | UnLoad-3Ph 25KVA DTR | As per relevent standard specification | 202 | EA | 202
73 | SWR10200 | 1 | Loading of 33/11 KV Current Transformers/ Potential Transformers. | Electrical work | LOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 165 | EA | 165
74 | SWR10266 | 3 | Loading of 33 KV10 KA LAs Station type. | Electrical work | LOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 41 | EA | 123
75 | SWR10584 | 3 | Unloading of 33 KV10 KA LAs Station type. | Electrical work | UNLOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 35 | EA | 105
76 | SWR10265 | 9 | Loading of 11 KV10 KA LAs Line type. | Electrical work | LOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 288
77 | SWR10583 | 9 | Unloading of 11 KV10 KA LAs Line type. | Electrical work | UNLOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 288
78 | SWR10264 | 3 | Loading of 11 KV10 KA LAs Station type. | Electrical work | LOADING of 11 KV,10 KA LAs Station type | As per relevent standard specification | 32 | EA | 96
79 | SWR10582 | 3 | Unloading of 11 KV10 KA LAs Station type. | Electrical work | UNLOADING of 11 KV,10 KA LAs Station typ | As per relevent standard specification | 32 | EA | 96
80 | SWR10239 | 2 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 252
81 | SWR10557 | 2 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 158
82 | SWR10238 | 9 | loading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 720
83 | SWR10556 | 9 | Unloading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 720
84 | SWR11224 | 4 | Loading and Unloading of 12V/24V Battery Set. | Electrical work | Load/Unload-12V/24V Battery Set | As per relevent standard specification | 23 | EA | 92
85 | SWR10402 | 1 | Erection of 11kv Potential Transformer sets complete including jumpering. The LV side of the PT shall be provided with proper fuse protection mounted in separate marshalling boxwith proper size cable glands etc. The box shall be mounted on the Substation structure. | Electrical work | Erection of 11kv three phase PT s | As per relevent standard specification | 800 | SET | 800
86 | SWR10518 | 1 | Unloading of 33/11 KV Current Transformers/ Potential Transformers | Electrical work | UNLOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 128 | EA | 128
87 | SWR10674 | 1 | Fixing of Distribution Box and Providing with proper Fuse protection system and reqired Cable Terminations at Station T/F LT side and AC/DC Panel and fixing meter. Power cable of adequate size shall be provided from station DTR to control room AC Panel. | Electrical work | Erection of LT distribution box | As per relevent standard specification | 1594.67 | EA | 1594.67
88 | SWR21750 | 1 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply and fixing of PT Marshalling box | As per relevent standard specification | 1139.85 | EA | 1139.85
89 | SMR40067 | 2 | Supply of Hand Gloves | Electrical work | Supply of Hand Gloves | As per relevent standard specification | 289 | SET | 578
90 | SMR40071 | 2 | Supply of Safety Helmets of standard make | Electrical work | Supply of Safety Helmet of standard make | As per relevent standard specification | 231 | EA | 462
91 | SMR40009 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for First coat of 1st GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 11995.5
92 | SWR10877 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 1st coat of Aluminium | Electrical work | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 4680.5
93 | SWR20904 | 20 | Supply & Providing of Panther T clamps. | Electrical work | Supply & Providing of Panther T clamps. | As per relevent standard specification | 320 | EA | 6400
94 | SMR40010 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for second coat of 2nd GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 7111.5
95 | SWR10879 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 2nd coat of Aluminium | Electrical work | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 2651
96 | SWR22092 | 8.85 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 33 kv line | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 6770.25 | 33KV LINE
97 | SWR10108 | 15 | Excavation of Pole pits of size 0.76x0.9x1.95 Mts' for 12.5 mts spun Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAV. OF PIT 0.75 M x 0.9 M x 1.95 M | As per relevent standard specification | 720 | EA | 10800
98 | SWR10107 | 103 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 72100
99 | SWR10112 | 60 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0") | As per relevent standard specification | 1680 | EA | 100800
100 | SWR10105 | 39 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 23400
101 | SWR10350 | 15 | Erection of 12.5 Mtr spun pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Earth work | Erection of Spun pole 12.5Mt | As per relevent standard specification | 4115.7 | EA | 61735.5
102 | SWR10319 | 15 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 75 x 8 mm MS Flat | Earth work | Fab Back clamps with 75 x 8 mm MS Flat | As per relevent standard specification | 31.62 | EA | 474.3
103 | SWR10978 | 163 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 678940.64
104 | SWR10343 | 39 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Earth work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 93600
105 | SWR10981 | 36 | Formation of 33 kv cut points (Vertical/Horizantal) including fixing of Clamps and top cleat and fixing of pin insulator complete with necessary hard wear for stud locations excluding the cost of pit Excavation and the pole shall be numbered with colour paint and earthing. | Electrical work | Horizontal Cut point for 33 KV line | As per relevent standard specification | 1759.5 | EA | 63342
106 | SWR10356 | 67.97 | Concreting the location after erection of 12.5/11 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.75X0.9X1.95 Mts)* 5 = 7.22 Cu.Mt and (0.75X0.75X2 Mts)* 54 = 60.75 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 447174.63
107 | SWR10366 | 8.85 | Paving of the 100 sqmm AAA conductor and stringing duly arranging temporary guys, tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pin binding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Earth work | Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevent standard specification | 12600.06 | KM | 111510.531
108 | SMR11488 | 220 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 25850
109 | SWR11180 | 163 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 70411.11
110 | SWR20308 | 39 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Earth work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 15884.31
111 | SWR10191 | 6 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 1212
112 | SWR10509 | 6 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 600
113 | SWR11860 | 6 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip. | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 16322.04
114 | SWR10150 | 2.015 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 1243.4565
115 | SWR10206 | 2.015 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 445.315
116 | SWR10524 | 2.015 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 372.775
117 | SWR10211 | 87 | Loading of 33 KV Pin insulators | Electrical work | LOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | KI | 261
118 | SWR10529 | 87 | Unloading of 33 KV Pin insulators | Electrical work | UNLOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | KI | 261
119 | SWR12416 | 36 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | KI | 72
120 | SWR10631 | 36 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | KI | 72
121 | SWR10618 | 36 | Loading of 33KV Metal parts bag of 25 nos. | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 2340
122 | SWR10632 | 36 | Unloading of 33 KV Metal parts bag of 25 nos. | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 2340
123 | SWR10354 | 95 | Erection of 33 kv Stay set complete including fixing of bow ,fixing and binding of Eye bolt, Anchor rod, guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. | Electrical work | Assembly and erection of Stay set 33kv | As per relevent standard specification | 684.53 | SET | 65030.35
124 | SWR20819 | 34.304 | Mass concreting with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for stay/stud locations .Using form boxes ( 0.45x0.45x1.265) *134= 34.304 cu mts | Civil work | Mass concreting of stay locations | As per relevent standard specification | 6579 | EA | 225686.016
125 | SWR21933 | 95 | Excavation of Stay pits of size 0.45x0.45x1.265 Mts' for burying the anchor rod with anchor plate of stay sets including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits any and leveling the site with out any lead.In all soils with Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting | Electrical work | Exc Stay pit 0.45x0.45x1.265M Hard Soil | As per relevent standard specification | 1271.18 | EA | 120762.1
126 | SWR22092 | 3.36 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 33 kv line | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 2570.4 | 11kv line
127 | SWR10108 | 21 | Excavation of Pole pits of size 0.76x0.9x1.95 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting | Earth work | EXCAV. OF PIT 0.75 M x 0.9 M x 1.95 M | As per relevent standard specification | 720 | EA | 15120
128 | SWR10105 | 11 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 6600
129 | SWR10107 | 30 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 21000
130 | SWR21933 | 32 | Excavation of Stay pits of size 0.45x0.45x1.265 Mts' for burying the anchor rod with anchor plate of stay sets including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits any and leveling the site with out any lead.In all soils with Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting | Earth work | Exc Stay pit 0.45x0.45x1.265M Hard Soil | As per relevent standard specification | 1271.18 | EA | 40677.76
131 | SWR10978 | 21 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Earth work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 87470.88
132 | SWR10342 | 11 | Erection of 8.0 Mts PSCC Poles complete with necessary hard ware for yard lighting excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Earth work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 16500
133 | SWR10343 | 30 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Earth work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 72000
134 | SWR10653 | 17 | Formation of 11 kv cut points (Vertical/Horizantal) including fixing of 11 KV Cross arms,clamps, strain insulators sets complete with hardware and stays (Bows and Eye-bolts), Excluding the cost of pit Excavation and pole erection. The contractor has to supply GI Bolts and Nuts. | Electrical work | Formatn of Horiz Cut point for 11KV line | As per relevent standard specification | 1350 | EA | 22950
135 | SWR10356 | 8.008 | Concreting the location after erection of 9.1/11 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.76X0.76X1.52 Mts)* 4 = 3.508 Cu.Mt and (0.75X0.75X2 Mts)* 4 = 4.5 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 52684.632
136 | SWR10356 | 13.312 | Mass concreting with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for stay/stud locations .Using form boxes ( 0.45x0.45x1.265) *52= 34.304 cu mts | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 87579.648
137 | SWR10365 | 1.01 | Paving of the conductor 55 Sqmm Single Circuit (3 Conductors) AAAC and stringing duly arranging temporary guys,tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pinbinding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing of 55sqmm 33/11kv Line 3 Cond | As per relevent standard specification | 8500 | KM | 8585
138 | SMR11488 | 150 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 17625
139 | SWR10206 | 1.271 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 280.891
140 | SWR10524 | 1.271 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 235.135
141 | SWR11248 | 185 | Loading 11KV Polymer Pin Insulator with GI pins | Electrical work | Load-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 185
142 | SWR11249 | 185 | Unloading 11KV Polymer Pin Insulator with GI pins | Electrical work | Unload-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 185
143 | SWR10134 | 1.271 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 746.7379
144 | SWR11862 | 2 | Transport of VCB , Control pannels, current transformater, bosster etc, above 20 KM and upto 30 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs >20 & <30Km | As per relevent standard specification | 3691.38 | EA | 7382.76
145 | SWR10191 | 2 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 404
146 | SWR10509 | 2 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 200
147 | SWR20307 | 11 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM. | Earth work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 2986.72
148 | SWR20308 | 30 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Earth work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 12218.7
149 | SWR11180 | 21 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Earth work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 9071.37
150 | SWR10228 | 34 | Loading of 11 KV V - Cross arms | Electrical work | LOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 136
151 | SWR10546 | 34 | Unloading of 11 KV V - Cross arms | Electrical work | UNLOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 136
152 | SWR12402 | 10 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 480
153 | SWR12421 | 10 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 480
154 | SWR10251 | 16 | Loading of 11 KV Top fittings | Electrical work | LOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 16
155 | SWR10569 | 16 | Unloading of 11 KV Top fittings | Electrical work | UNLOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 16
156 | SWR12416 | 10 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | KI | 20
157 | SWR10631 | 10 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | KI | 20
158 | SWR10353 | 32 | Erection of 11 kv Stay set complete including fixing of bow, fixing and binding of Eye bolt,Anchor rod,guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. The contractor has to supply GI Bolts and Nuts. | Earth work | Assembly and erection of Stay set11kv&LT | As per relevent standard specification | 606.85 | SET | 19419.2
159 | SWR10703 | 1.05 | Paving of the conductor 55 Sqmm double Circuit (6 Conductors) AAAC and stringing duly arranging temporary guys,tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pinbinding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing of 55sqmm 33/11kv Line 6 Cond | As per relevent standard specification | 16000 | KM | 16800
160 | SWR10392 | 2 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 9000 | DP STR
161 | SWR10105 | 8 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Electrical work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 4800
162 | SWR10107 | 4 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 2800
163 | SWR10343 | 8 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 19200
164 | SWR10978 | 4 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 16661.12
165 | SWR10356 | 7.88 | Concreting the location after erection of 9.1/11 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 51842.52
166 | SMR11488 | 10 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 1175
167 | SWR10206 | 0.68 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 150.28
168 | SWR10524 | 0.68 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 125.8
169 | SWR10134 | 0.68 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.51 | TO | 399.5068
170 | SWR20308 | 8 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 3258.32
171 | SWR11180 | 4 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 1727.88
172 | SWR12402 | 1 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 48
173 | SWR12421 | 1 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 48
174 | SWR12416 | 1 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | KI | 2
175 | SWR10631 | 1 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | KI | 2
176 | SMR11482 | 4 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 13944
177 | SWR10357 | 4 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.6M dia x 0.5 M height | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 4936.8
178 | SMR11485 | 64 | Supply of earthing GI Flat 25X3 mm including material | Earth work | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 6720
179 | SWR10239 | 2 | LOADING of 33 KV AB SWCH Con 400/800 A | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 252
180 | SWR10557 | 2 | UNLOADING of 33 KV AB SWCH Con 400/800 A | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 158
181 | SWR10393 | 4 | Erection of 11kV AB Switches 800/400 Amps includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 12800 | 11KV LINE ABS
182 | SMR11488 | 8 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 940
183 | SWR10206 | 0.274 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 220.99 | TO | 60.5513
184 | SWR10524 | 0.274 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 50.69
185 | SWR10134 | 0.274 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 160.9805
186 | SMR11484 | 4 | Supply of C I earth pipe of size 50mm dia, 2 mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 50mm dia 2m long | As per relevent standard specification | 2441 | EA | 9764
187 | SWR11222 | 8 | Loading/Unloading of C I earth pipe of size 80/50mm dia, 2 mtrs long for earth electrode | Electrical work | Load/Unload-CI pipe 80/50 mm dia 2mt L | As per relevent standard specification | 18 | EA | 144
188 | SWR34671 | 4 | Providing of collar rings of 450mm dia at 4 pole structure | Electrical work | Collar/ Rings of 450mm dia | As per relevent standard specification | 260 | EA | 1040
189 | SMR11485 | 40 | Supply of earthing GI Flat 25X3 mm including material | Electrical work | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 4200
190 | SWR10238 | 4 | loading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 320
191 | SWR10556 | 4 | Unloading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 320
192 | SWR10107 | 4 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 2800 | 4 POLE
193 | SWR10105 | 4 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 2400
194 | SWR10978 | 4 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 16661.12
195 | SWR10343 | 4 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 9600
196 | SWR10356 | 8.008 | Concreting the location after erection of 9.1/11 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.76X0.76X1.52 Mts)* 4 = 3.508 Cu.Mt and (0.75X0.75X2 Mts)* 4 = 4.5 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 52684.632
197 | SWR10868 | 0.7 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the ply and fabrication of 6mm base and top plate for Box pole to theRS Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection | Electrical work | Fabrication of struc.with power drilling | As per relevent standard specification | 6852 | TO | 4796.4
198 | SWR10404 | 5 | Erection of 33kV and 11kV Strung Bus with Panther (200Sqmm) ACSR Conductor: Erection of 33kV and 11kV Bus over the Substation structures with 200sqmm Panther ACSR conductor and giving Jumpers to connect the Switch gear by providing the suitable T clamps and round clamps suitable to Post type insulators & Insulators. | Electrical work | Stringing of bus with panther conductor | As per relevent standard specification | 327.68 | M | 1638.4
199 | SWR10392 | 2 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 9000
200 | SWR10396 | 1 | Erection of 33KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 33kv LA stn type incl earthing | As per relevent standard specification | 880 | SET | 880
201 | SMR11482 | 4 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 13944
202 | SWR10357 | 4 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 4936.8
203 | SMR11488 | 25 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 2937.5
204 | SMR40036 | 12 | Sup PG clamps for panther 2 bolted 600 A | Electrical work | SupPG clamps for panther 2 bolted 600 A | As per relevent standard specification | 100 | EA | 1200
205 | SWR10239 | 2 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 252
206 | SWR10557 | 2 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 158
207 | SWR10150 | 0.89 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 549.219
208 | SWR10206 | 0.89 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 196.69
209 | SWR10524 | 0.89 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 164.65
210 | SWR10263 | 4 | LOADING of CI Earth pipe upto 2.7 Mtr | Electrical work | LOADING of CI Earth pipe upto 2.7 Mtr | As per relevent standard specification | 29 | EA | 116
211 | SWR10581 | 4 | UNLOADING of CI Earth pipe upto 2.7 Mtr | Electrical work | UNLOADING of CI Earth pipe upto 2.7 Mtr | As per relevent standard specification | 29 | EA | 116
212 | SWR34179 | 16 | Hire-JCB to Level & Clear the Site | Civil work | Hire-JCB to Level & Clear the Site | As per relevent standard specification | 2165.7 | H | 34651.2
213 | SWR33015 | 102.9 | Excavation in Ordinary Soil | Civil work | Excavation in Ordinary Soil | As per relevent standard specification | 366 | M3 | 37661.4
214 | SWR33028 | 19.2 | PCC with 40mm Metal (1:4:8) | Civil work | PCC with 40mm Metal (1:4:8) | As per relevent standard specification | 4303 | M3 | 82617.6
215 | SWR33041 | 132.6 | CRS Masonary CM(1:6) 2nd Sort | Civil work | CRS Masonary CM(1:6) 2nd Sort | As per relevent standard specification | 4257 | M3 | 564478.2
216 | SWR33068 | 23.1 | Brick Masonary in CM(1:6) GFloor | Civil work | Brick Masonary in CM(1:6) GFloor | As per relevent standard specification | 8213 | M3 | 189720.3
217 | SWR33052 | 667.6 | S&Filling with Borrowed Gravel | Civil work | S&Filling with Borrowed Gravel | As per relevent standard specification | 485 | M3 | 323786
218 | SWR33098 | 5.9 | RCC Footing: M20Gr, Steel Centering | Civil work | RCC Footing: M20Gr, Steel Centering | As per relevent standard specification | 8552 | M3 | 50456.8
219 | SWR33100 | 2.9 | RCC Column GF: M20Gr, Steel Centering | Civil work | RCC Column GF: M20Gr, Steel Centering | As per relevent standard specification | 11427 | M3 | 33138.3
220 | SWR33099 | 2 | RCC Plinth Beam: M20Gr, Steel Centering | Civil work | RCC Plinth Beam: M20Gr, Steel Centering | As per relevent standard specification | 11169 | M3 | 22338
221 | SWR33107 | 0.9 | RCC Lintel GF: M20Gr, Steel Centering | Civil work | RCC Lintel GF: M20Gr, Steel Centering | As per relevent standard specification | 11618 | M3 | 10456.2
222 | SWR33114 | 13.5 | RCC Sunshade GF: M20Gr, Steel Centering | Civil work | RCC Sunshade GF: M20Gr, Steel Centering | As per relevent standard specification | 1229 | M2 | 16591.5
223 | SWR33121 | 2.9 | RCC Roof Beam GF: M20Gr, Steel Centering | Civil work | RCC Roof Beam GF: M20Gr, Steel Centering | As per relevent standard specification | 11227 | M3 | 32558.3
224 | SWR33128 | 10.2 | RCC Roof Slab GF: M20Gr, Steel Centering | Civil work | RCC Roof Slab GF: M20Gr, Steel Centering | As per relevent standard specification | 10741 | M3 | 109558.2
225 | SWR33144 | 2.5 | Reinforcement Steel Fe 415/500 | Civil work | Reinforcement Steel Fe 415/500 | As per relevent standard specification | 72726 | TON | 181815
226 | SWR33163 | 404.66 | Plastering 20mm (16mm+4mm)GFloor | Civil work | Plastering 20mm (16mm+4mm)GFloor | As per relevent standard specification | 434 | M2 | 175622.44
227 | SWR33184 | 142.5 | Raised Pointing to CRS Masonary CM(1:3) | Civil work | Raised Pointing to CRS Masonary CM(1:3) | As per relevent standard specification | 98 | M2 | 13965
228 | SWR33156 | 78.1 | Impervious Coat 20mm CM(1:3) GFloor | Civil work | Impervious Coat 20mm CM(1:3) GFloor | As per relevent standard specification | 462 | M2 | 36082.2
229 | SWR33264 | 5.7 | S&F MT Wood Frame & Door-Laminate | Civil work | S&F MT Wood Frame & Door-Laminate | As per relevent standard specification | 6871 | M2 | 39164.7
230 | SWR33278 | 5.76 | S&F Powder Coated Al Window | Civil work | S&F Powder Coated Al Window | As per relevent standard specification | 3572 | M2 | 20574.72
231 | SWR33310 | 6.25 | S&F of MS Safety Grill | Civil work | S&F of MS Safety Grill | As per relevent standard specification | 2622 | M2 | 16387.5
232 | SWR33219 | 39.2 | Polished Shabad Flooring 20mm CM(1:3) | Civil work | Polished Shabad Flooring 20mm CM(1:3) | As per relevent standard specification | 541 | M2 | 21207.2
233 | SWR33236 | 10.7 | Polished Shabad Skirting CM(1:3) | Civil work | Polished Shabad Skirting CM(1:3) | As per relevent standard specification | 610 | M2 | 6527
234 | SWR33029 | 32.5 | PCC with 40mm Metal (1:3:6) | Civil work | PCC with 40mm Metal (1:3:6) | As per relevent standard specification | 4582 | M3 | 148915
235 | SWR33030 | 6.8 | PCC with 20mm Metal (1:2:4) | Civil work | PCC with 20mm Metal (1:2:4) | As per relevent standard specification | 5715 | M3 | 38862
236 | SWR33057 | 49.5 | S&Spreading of 20mm HBG Metal | Civil work | S&Spreading of 20mm HBG Metal | As per relevent standard specification | 1618 | M3 | 80091
237 | SWR33403 | 110 | S&F MS Security Fencing Mesh (2"X2") | Civil work | S&F MS Security Fencing Mesh (2"X2") | As per relevent standard specification | 2110 | M2 | 232100
238 | SWR33404 | 10.55 | S&F MS Gate | Civil work | S&F MS Gate | As per relevent standard specification | 4676.9 | M2 | 49341.295
239 | SWR33333 | 121 | Painting with OBD 2Coats+Primer | Civil work | Painting with OBD 2Coats+Primer | As per relevent standard specification | 115 | M2 | 13915
240 | SWR33336 | 178.4 | Painting SnowCem/Apex 2 Coats+Primer | Civil work | Painting SnowCem/Apex 2 Coats+Primer | As per relevent standard specification | 205 | M2 | 36572
241 | SWR33329 | 175.9 | Painting with SuryaCem of 3 Coat | Civil work | Painting with SuryaCem of 3 Coat | As per relevent standard specification | 73 | M2 | 12840.7
242 | SWR33442 | 30 | S&F Conceal PVC Pipe 25mm dia in Slab | Civil work | S&F Conceal PVC Pipe 25mm dia in Slab | As per relevent standard specification | 90 | M | 2700
243 | SWR33441 | 20 | S&F Conceal PVC Pipe 25mm dia in Wall | Civil work | S&F Conceal PVC Pipe 25mm dia in Wall | As per relevent standard specification | 93 | M | 1860
244 | SWR33457 | 15 | S&F Modular Switch LP,FP,EFP for NRBuild | Civil work | S&F Modular Switch LP,FP,EFP for NRBuild | As per relevent standard specification | 602 | EA | 9030
245 | SWR33461 | 2 | S&F Modular 3/2pin 6A Sockets | Civil work | S&F Modular 3/2pin 6A Sockets | As per relevent standard specification | 493 | EA | 986
246 | SWR33464 | 2 | S&F Modular 3pin 16/6A Sockets | Civil work | S&F Modular 3pin 16/6A Sockets | As per relevent standard specification | 455 | EA | 910
247 | SWR33484 | 4 | S&F Batten Holder | Civil work | S&F Batten Holder | As per relevent standard specification | 224 | EA | 896
248 | SWR33545 | 4 | S&F 20W LED Retro Tube Light | Civil work | S&F 20W LED Retro Tube Light | As per relevent standard specification | 876.5 | EA | 3506
249 | SWR33494 | 90 | S&R 2 of 14/0.3mm (1.0sqmm) (FR) | Civil work | S&R 2 of 14/0.3mm (1.0sqmm) (FR) | As per relevent standard specification | 49 | M | 4410
250 | SWR33497 | 30 | S&R 2 of 36/0.3mm (2.5sqmm) (FR) | Civil work | S&R 2 of 36/0.3mm (2.5sqmm) (FR) | As per relevent standard specification | 100 | M | 3000
251 | SWR33520 | 1 | S&F 8wySPNDB IP-20,10kA-6-32A SPMCB 4No | Civil work | S&F 8wySPNDB IP-20,10kA-6-32A SPMCB 4No | As per relevent standard specification | 5368 | EA | 5368
252 | SWR33596 | 1 | Provd-Independent Earthing | Civil work | Provd-Independent Earthing | As per relevent standard specification | 5169 | EA | 5169
253 | SWR33597 | 15 | S&R No.8 SWG Copper Wire | Civil work | S&R No.8 SWG Copper Wire | As per relevent standard specification | 153 | M | 2295
254 | SWR33563 | 2 | S&F 1200mm (48'') Sweep Ceiling Fan | Civil work | S&F 1200mm (48'') Sweep Ceiling Fan | As per relevent standard specification | 2225 | EA | 4450
255 | SWR33224 | 13.7 | Ceramic Tile Flooring 20mm CM(1:3) | Civil work | Ceramic Tile Flooring 20mm CM(1:3) | As per relevent standard specification | 949 | M2 | 13001.3
256 | SWR34311 | 1 | S&F Orissa Pan WC 580mmx440mm | Civil work | S&F Orissa Pan WC 580mmx440mm | As per relevent standard specification | 2207 | EA | 2207
257 | SWR34386 | 2 | S&F Floor Trap (Bell Mouth) 110mm | Civil work | S&F Floor Trap (Bell Mouth) 110mm | As per relevent standard specification | 269 | EA | 538
258 | SWR34382 | 2 | S&F 90mm dia Plain Bend PVC/SWR Pipe | Civil work | S&F 90mm dia Plain Bend PVC/SWR Pipe | As per relevent standard specification | 84 | EA | 168
259 | SWR34385 | 1 | S&F 75mm dia Door Bend PVC/SWR Pipe | Civil work | S&F 75mm dia Door Bend PVC/SWR Pipe | As per relevent standard specification | 81 | EA | 81
260 | SWR34286 | 1 | S&F 150mmx100mm SWG Gully Trap | Civil work | S&F 150mmx100mm SWG Gully Trap | As per relevent standard specification | 749 | EA | 749
261 | SWR34377 | 6 | S&F 110mm dia 3M 1Socket PVC/SWR Pipe | Civil work | S&F 110mm dia 3M 1Socket PVC/SWR Pipe | As per relevent standard specification | 428 | M | 2568
262 | SWR34453 | 1 | S&F 4" dia PVC Cowl | Civil work | S&F 4" dia PVC Cowl | As per relevent standard specification | 23 | EA | 23
263 | SWR34444 | 1 | Construct- 4' dia & 5' Ht Soak Pit | Civil work | Construct- 4' dia & 5' Ht Soak Pit | As per relevent standard specification | 4951 | EA | 4951
264 | SWR34362 | 150 | S&F 22.20mm OD CPVC Pipe-SDR 11 | Civil work | S&F 22.20mm OD CPVC Pipe-SDR 11 | As per relevent standard specification | 417 | M | 62550
265 | SWR34363 | 100 | S&F 28.60mm OD CPVC Pipe-SDR 11 | Civil work | S&F 28.60mm OD CPVC Pipe-SDR 11 | As per relevent standard specification | 514 | M | 51400
266 | SWR34344 | 24 | S&F-15mm GM/Bronze Ball Valve | Civil work | S&F-15mm GM/Bronze Ball Valve | As per relevent standard specification | 230 | EA | 5520
267 | SWR34345 | 1 | S&F-20mm GM/Bronze Ball Valve | Civil work | S&F-20mm GM/Bronze Ball Valve | As per relevent standard specification | 331 | EA | 331
268 | SWR34346 | 2 | S&F-25mm GM/Bronze Ball Valve | Civil work | S&F-25mm GM/Bronze Ball Valve | As per relevent standard specification | 466 | EA | 932
269 | SWR34329 | 4 | S&F-15mm Bib Tap 400gm Full turn | Civil work | S&F-15mm Bib Tap 400gm Full turn | As per relevent standard specification | 275 | EA | 1100
270 | SWR34375 | 500 | S&F Polyethylene Water Storage Tank | Civil work | S&F Polyethylene Water Storage Tank | As per relevent standard specification | 10 | L | 5000
271 | SWR33746 | 1 | Supply of Table 4'x2' with MS Frame | Civil work | Supply of Table 4'x2' with MS Frame | As per relevent standard specification | 4350 | EA | 4350
272 | SWR33857 | 1 | Supply of S-Type Chair | Civil work | Supply of S-Type Chair | As per relevent standard specification | 4035 | EA | 4035
273 | SWR33858 | 2 | Supply of PVC Chair | Civil work | Supply of PVC Chair | As per relevent standard specification | 1200 | EA | 2400
274 | SWR33422 | 3 | S&F Glow Sign Board | Civil work | S&F Glow Sign Board | As per relevent standard specification | 3735 | M2 | 11205
275 | SWR33421 | 1.35 | S&F MS Board | Civil work | S&F MS Board | As per relevent standard specification | 4545 | M2 | 6135.75
276 | SWR33054 | 71.42 | S&Filling with Borrowed Stone Dust | Civil work | S&Filling with Borrowed Stone Dust | As per relevent standard specification | 1028 | M3 | 73419.76
277 | SWR33415 | 7.3 | S&F RCC Hume Pipe of 450mm dia | Civil work | S&F RCC Hume Pipe of 450mm dia | As per relevent standard specification | 1345 | M | 9818.5
278 | SWR33406 | 150 | S&F RCC Fencing Pole 0.115mx0.115mx2.7m | Civil work | S&F RCC Fencing Pole 0.115mx0.115mx2.7m | As per relevent standard specification | 1443 | EA | 216450
279 | SWR33405 | 25 | S&F RCC Fencing Pole 0.1mx0.1mx1.8m | Civil work | S&F RCC Fencing Pole 0.1mx0.1mx1.8m | As per relevent standard specification | 1299 | EA | 32475
280 | SWR33407 | 300 | S&F Barbed Wire 8H & 2Cross | Civil work | S&F Barbed Wire 8H & 2Cross | As per relevent standard specification | 260 | M | 78000
281 | SWR33425 | 1 | Provd-Supply of Electricity to Site | Civil work | Provd-Supply of Electricity to Site | As per relevent standard specification | 5678 | EA | 5678
282 | SWR33608 | 1 | Geophysical Investgation Charges | Civil work | Geophysical Investgation Charges | As per relevent standard specification | 7000 | EA | 7000
283 | SWR33609 | 90 | Drilling-165mm Bore Well 0 to 90M | Civil work | Drilling-165mm Bore Well 0 to 90M | As per relevent standard specification | 336 | M | 30240
284 | SWR34830 | 30 | Drill-165mm Bore Well 90M to 120M | Civil work | Drill-165mm Bore Well 90M to 120M | As per relevent standard specification | 389 | M | 11670
285 | SWR34831 | 30 | Drill-165mm Bore Well 120M to 150M | Civil work | Drill-165mm Bore Well 120M to 150M | As per relevent standard specification | 407 | M | 12210
286 | SWR33611 | 30 | S&F 160mm dia PVC Casing | Civil work | S&F 160mm dia PVC Casing | As per relevent standard specification | 1650 | M | 49500
287 | SWR33636 | 1 | S&E SP SubMrsbl Pumpset 2.0HP 30 Stages | Civil work | S&E SP SubMrsbl Pumpset 2.0HP 30 Stages | As per relevent standard specification | 34894 | EA | 34894
288 | SWR33641 | 60 | S&R 3C 2.5sqmm Flat Copper Cable | Civil work | S&R 3C 2.5sqmm Flat Copper Cable | As per relevent standard specification | 210 | M | 12600
289 | SWR33644 | 1 | S&E D.O.L Starter 250V Single Phase | Civil work | S&E D.O.L Starter 250V Single Phase | As per relevent standard specification | 2400 | EA | 2400
290 | SWR34203 | 1 | Supply & ixing of Flange Clamps | Civil work | Supply & ixing of Flange Clamps | As per relevent standard specification | 191 | EA | 191
291 | SWR34410 | 178 | S&F-HDPE Pipe 40mm dia 16kg/sqcm-SDR 9 | Civil work | S&F-HDPE Pipe 40mm dia 16kg/sqcm-SDR 9 | As per relevent standard specification | 155 | M | 27590
292 | SWR34470 | 173.5 | Seigniorage Charges - Sand | Civil work | Seigniorage Charges - Sand | As per relevent standard specification | 40 | M3 | 6940
293 | SWR34471 | 151.5 | Seigniorage Charges - Metal | Civil work | Seigniorage Charges - Metal | As per relevent standard specification | 97.5 | M3 | 14771.25
294 | SWR34472 | 667.6 | Seigniorage Charges - Gravel | Civil work | Seigniorage Charges - Gravel | As per relevent standard specification | 30 | M3 | 20028
Total amount (Excluding 18%GST) | [8 empty] | 7709539.051
18% GST | [8 empty] | 1387717.0292
Total amount (Including 18%GST) | [8 empty] | 9097256.0801