## SD-IV Schedule
Name of the work: Providing of second alternate source to 33/11kV Ravindra Society Indoor SS from 132/33kV Khaitalapur EHT SS which involves laying of 33KV 3X400sq.mm XLPE UG Cable (Double Run) for a distance of 5KM pertaining to Madhapur Lines Section & Sub Division of Banjarahills Lines Division of SCADA circle and work executed by the Master plan SD-IV Section & Sub-Division of MP-1 Division of Hyderabad Masterplan Circle under T&D Improvements to original works (Summer Action Plan 2026).
WBS No : T-2527-12-01-01-01-001
S C H E D U L E
S No. | Estimate Quantity | Item Detailed Specification Description | Work Type | Item Short Description | Service Code | Rate | UOM | Amount
1 | 5 | Survey line & cabel including peg mark & tree clearing | Electrical | Labour | SWR22092 | 765 | KM | 3825 | SS LABOUR OLD
2 | 34 | Loading of 11KV/33KV XLPE UG Cable Drum for all sizes | Electrical | Labour | SWR11230 | 1024 | DR | 34816
3 | 17 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Upto 10 Km with Lorry for each trip | Electrical | Labour | SWR11860 | 2720.34 | EA | 46245.78
4 | 34 | Un loading of 11KV/33KV XLPE UG Cable Drum for all sizes | Electrical | Labour | SWR11231 | 1024 | DR | 34816
5 | 4100 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters,providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,Along the CC / BT multi layer road requiring compressor for 33 KV 3x400 Sqmm Cable | Electrical | Labour | SWR11980 | 1388.84 | M | 5694244
6 | 200 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters,providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) for 33 KV 3x400 Sqmm Cable | Electrical | Labour | SWR11988 | 1587.07 | M | 317414
7 | 100 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters,providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC for 33 KV 3x400 Sqmm Cable | Electrical | Labour | SWR11972 | 749 | M | 74900
8 | 100 | Laying of 33KV XLPE UG cable Double Run of Size in Hard Rock(1.2*0.5x1=0.6cum) | Electrical | Labour | SWR11002 | 1430 | RMT | 143000
9 | 1000 | Laying of 33&11KV UG cable by HDD (Horizontal Directional Drilling) in normal soil method with casing HDPE pipe of 160mm PN4 PE 80 as per IS4984 | Electrical | Labour | SWR11001 | 6993 | M | 6993000
10 | 60 | Raising of double run 33KV 3x400sqmm UG cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) 33 KV 3x400 Sqmm Cable | Electrical | Supply | SWR12004 | 323.85 | M | 19431
11 | 4400 | Laying of 2nd Cable in Excavated Trench | Electrical | Supply | SWR10988 | 204.1 | M | 898040
12 | 46 | Supply & Erection of Smart RFID marker | Electrical | Supply | SWR25089 | 2745 | EA | 126270
13 | 36 | Making of 33KV 3X400Sq.mm XLPE UG Cable Straight through joints | Electrical | Labour | SWR10382 | 5700.78 | EA | 205228.08
14 | 1200 | Supply of 6" B Class GI pipe 5mm thck 20Kg/M | Electrical | Labour | SMR40081 | 1344 | M | 1612800
15 | 400 | Supply of 6" DWC pipe | Electrical | Labour | SMR11610 | 1012 | M | 404800
16 | 800 | Supply ofHume pipe 9" size | Electrical | Labour | SMR40001 | 125 | M | 100000
17 | 14 | Making of 33KV 3X400Sq.mm XLPE UG Cable Outdoor/Indoor End Termination | Electrical | Labour | SWR10387 | 2764.76 | EA | 38706.64
18 | 5000 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Electrical | Labour | SWR21903 | 30 | M | 150000
19 | 1.2 | LOADING of MS Channel,Angles,Flats&Rods | Electrical | Labour | SWR10206 | 221 | TO | 265.2
20 | 1.2 | UNLOADING of MS Channel,Angles,Flats&Rod | Electrical | Labour | SWR10524 | 185 | TO | 222
21 | 19 | Loading of R.S. Joists 175 x 85 mm | Electrical | Labour | SWR10204 | 76 | EA | 1444
22 | 5.95 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Electrical | Labour | SWR10132 | 412.08 | TO | 2451.876
23 | 19 | Un loading of R.S. Joists 175 x 85 mm | Electrical | Labour | SWR10522 | 50 | EA | 950
24 | 9 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Electrical | Labour | SWR10642 | 512.55 | EA | 4612.95
25 | 10 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Electrical | Labour | SWR10640 | 1132 | EA | 11320
26 | 10 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Electrical | Labour | SWR11040 | 990.68 | EA | 9906.8
27 | 9 | Erection of Box pole 9/10/11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical | Labour | SWR11266 | 2643.83 | EA | 23794.47
28 | 78.13 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 75x8mm / 75 x 12 mm | Electrical | Labour | SWR10918 | 50 | RMT | 3906.5
29 | 10.5 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Electrical | Labour | SWR10356 | 6579 | M3 | 69079.5
30 | 0.31 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Electrical | Labour | SWR11890 | 3893 | M3 | 1206.83
31 | 0.825 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Electrical | Labour | SWR10869 | 3426 | TO | 2826.45
32 | 3 | Erection of 33 KV LAS station/Line type including earthing | Electrical | Labour | SWR10396 | 880 | SET | 2640
33 | 3 | Loading of 33KV 800 Amps AB Switch | Electrical | Supply | SWR10239 | 126 | EA | 378
34 | 3 | Un loading of 33KV 800 Amps AB Switch | Electrical | Labour | SWR10557 | 79 | EA | 237
35 | 3 | Erection of 33 KV AB Switch including alignment and earthing | Electrical | Labour | SWR10392 | 4500 | EA | 13500
36 | 11 | Supply of CI Pipe earthing 80mm dia 2.75m long | Electrical | Supply | SMR11483 | 2789 | EA | 30679
37 | 11 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and | Electrical | Labour | SWR10357 | 1234.2 | EA | 13576.2
38 | 11 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Electrical | Supply | SWR10359 | 386 | EA | 4246
39 | 42 | Supply of Pre-cast cable Joint markersSupply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Electrical | Labour | SMR40085 | 484 | EA | 20328
40 | 10 | Painting of feeder name on support including cost of paint | Electrical | Labour | SWR12101 | 53 | EA | 530
41 | 100 | Supply of GI Bolts & Nuts,Washers etc., | Electrical | Labour | SMR11488 | 117.5 | KG | 11750
42 | 3 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical | Labour | SWR10881 | 142 | EA | 426
43 | 3 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Electrical | Supply | SWR12331 | 146.63 | EA | 439.89
44 | 72 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Electrical | Labour | SWR10356 | 6579 | M3 | 473688
45 | 1 | Erection of RS Joist 175 x 85 mmpole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical | Labour | SWR10346 | 1934 | EA | 1934
Total (Excl. GST) Rs. | [7 empty] | 17603875.166 | 17603875.166
18% GST Rs. | [7 empty] | 3168697.5299
Total ( Incl. GST) Rs. | [7 empty] | 20772572.6959 | 21881286.18 | -1108713.4841
|  |  | 2101655.95 |  |  |  |  | 33998770
9632925.29
|  |  | 5876135 |  |  |  |  | -13226197.3041
932746.63
18543462.87