## Schedule
SCHEDULE
Name of the Work :- Providing of 33KV alternate source (new 33KV feeder) to 33/11kV Khilwath SS from 132/33KV Seetharambagh EHT SS duly extending to 33/11kV Petlaburz SS & 33/11kV Salarjung SS by laying of 33KV 3X400Sq.mm XLPE UG Cable from the EHT SS to near Nayapul Bridge & Nayapul Bridge to 33/11kV Khilwath, Petlaburz and Salarjung sub-stations respectively in Hyderabad South operation division of Hyderabad South Circle and the work executed by the Master Plan SD-III of Master plan Division-II in Master plan Hyderabad Circle under T&D Improvements to original works (Summer Action Plan 2026).
WBS Element :- T-2527-12-02-03-01-004
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT (Rs.)
1 | 7 | Survey line&cabl inc peg mark,tree clear&trail pits | Elect | Labour | SWR22092 | 765 | KM | 5355
2 | 38 | Loading of 11KV/33KV XLPE UG Cable Drums for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 38912
3 | 19 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators,transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)- Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11865 | 5839.5 | EA | 110950.5
4 | 38 | Un loading of 11KV/33KV XLPE UG Cable Drum for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 38912
5 | 3800 | Excavation & laying of UG Cable (Double Run) - Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally 4" for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and liftetc - (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs &33 KV - 1.20 mtrs.- Along the CC / BT multi layer road requiring compressor - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11980 | 1388.84 | M | 5277592
6 | 200 | Excavation & laying of UG Cable (Double Run) - Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally 4" for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and liftetc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs &33 KV - 1.20 mtrs.-.Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe)-33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11988 | 1587.07 | M | 317414
7 | 200 | Laying of 33&11KV UG cable by HDD method with casing HDPE pipe of 160mm PN4 PE 80 as per IS4984 | Elect | Labour | SWR11001 | 6993 | M | 1398600
8 | 4000 | Laying of 2nd Cable in Excavated Trench | Elect | Labour | SWR10988 | 204.1 | M | 816400
9 | 3000 | Excavation & laying of UG Cable (single Run) - Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs &33 KV - 1.20 mtrs.- Along the CC / BT multi layer road requiring compressor - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11927 | 1175.56 | M | 3526680
10 | 40 | Raising of double run 33KV 3x400sqmm UG cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR12004 | 323.85 | M | 12954
11 | 70 | Raising of Single run 33KV 3x400sqmm UG cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11954 | 135.66 | M | 9496.2
12 | 70 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 192150
13 | 1000 | Supply of 6" B class GI pipe 150 NB GI Pipe 4.85 mm thickness, 19.2 KG/Mtr | Elect | Supply | SMR40081 | 1344 | M | 1344000
14 | 1000 | supply of 6" DWC pipe | Elect | Supply | SMR11610 | 1012 | M | 1012000
15 | 6500 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 195000
16 | 17 | Making of 33KV 3X400Sq.mm XLPE UG Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 47000.92
17 | 38 | Making of 33KV 3X400Sq.mm XLPE UG Cable Straight through joints | Elect | Labour | SWR10382 | 5700.78 | EA | 216629.64
18 | 1 | Construction of plinth for 3way RMUs etc | Elect | Labour | SWR20871 | 6000 | EA | 6000
19 | 1 | Erection of 33KV 3 Way RMU | Elect | Labour | SWR11335 | 5775 | EA | 5775
20 | 2 | Supply of CI eath pipe with 50mm dia,2.0 M Length | Elect | Supply | SMR11484 | 2441 | EA | 4882
21 | 10 | Supply of GI Flat 25X3 mm | Elect | Supply | SMR11485 | 105 | KG | 1050
22 | 20 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete | Elect | Labour | SWR12125 | 14.03 | M | 280.6
23 | 2 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 2468.4
24 | 2 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 772
25 | 2 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 106
26 | 540 | Laying of the cable along the footpath through by removing & relaying of slabsincluding material with necessary plastering. - 33kV 1x400 Sqmm Cu cable | Elect | Labour | SWR11971 | 308.55 | M | 166617
27 | 160 | Raising of Single run 33kV 1x400 Sqmm Cu cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11962 | 121.13 | M | 19380.8
28 | 4 | Supply of 33KV 1Cx400Sqmm PlugTerminationKit | Elect | Supply | SMR24773 | 90915 | EA | 363660
29 | 4 | Instalation of 33KV 1Cx400Sqmm PlugTerminationKit | Elect | Labour | SWR24773 | 15675 | EA | 62700
30 | 4 | Supply of 33KV 1Cx400Sqmm O/d Cb End Kit | Elect | Supply | SMR24774 | 6792.5 | EA | 27170
31 | 4 | Instalation of 33KV 1Cx400Sqmm O/d Cb End Kit | Elect | Labour | SWR24774 | 3030.5 | EA | 12122
32 | 2.4 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 530.4
33 | 2.4 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 444
34 | 36 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 2736
35 | 11.4 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 4697.712
36 | 36 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 1800
37 | 18 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 9225.9
38 | 18 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 20376
39 | 18 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 17832.24
40 | 6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation and concreting - Erection of 33KV DP Structure with 175x85/150x75mm RS joist | Elect | Labour | SWR11276 | 5670 | SET | 34020
41 | 6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 15862.98
42 | 375 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 15375
43 | 18.36 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 120790.44
44 | 0.372 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893.01 | M3 | 1448.1997
45 | 1.5 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 5139
46 | 6 | Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10239 | 126 | EA | 756
47 | 6 | Un loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10557 | 79 | EA | 474
48 | 6 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 27000
49 | 6 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 879.78
50 | 6 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 852
51 | 18 | Loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10266 | 41 | EA | 738
52 | 18 | Un loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10584 | 35 | EA | 630
53 | 6 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | SET | 5280
54 | 12 | Supply of CI eath pipe with 80mm dia,2.75 M Length | Elect | Labour | SMR11483 | 2789 | EA | 33468
55 | 12 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 14810.4
56 | 12 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 4632
57 | 6 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 318
58 | 60 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 7050
Total (Excl. GST) Rs. | [7 empty] | 15580196.1117
18% GST Rs. | [7 empty] | 2804435.3001
Total (Incl. GST) Rs. | [7 empty] | 18384631.4118