## Road nO.13 schedule
SCHEDULE
Name of the Work : Providing of 33KV Road No. 13 feeder (emanating from 132/33KV Erramanzil(NIMS) EHTSS) as an 2nd alternate source of supply to 33/11KV Road No.13 SS by laying of 2.7 KM of 33KV 3X400Sq.mm XLPE UG Cable (double run) from 132/33KV Erramanzil (NIMS) EHT SS to 33/11KV Road No.13 SS by erection of n/p 33KV VCB and 4-pole structure at 33/11KV Erramanzil SS of Banjarahills Circle of Masterplan SD-4 section & Sub-Division in Masterplan-I Division of Masterplan Circle, Hyderbad under T&D Improvement works.
WBS Element : T-2331-12-01-01-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 18 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 18432
2 | 18 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 18432
3 | 9 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 29697.3
4 | 1690 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, Sqmm Cable 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. - Along the CC / BT multi layer road requiring compressor- 33 KV 3x400 Sqmm | Elect | Labour | SWR11980 | 1388.84 | M | 2347139.6
5 | 200 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, Sqmm Cable 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs - Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) - 33 KV 3x400 Sqmm | Elect | Labour | SWR11988 | 1587.07 | M | 317414
6 | 810 | Hard Rock Cutting - Laying of 33KV XLPE UG cable Double Run of Size in Hard Rock(1.2*0.5x1=0.6cum) | Elect | Labour | SWR11002 | 1430 | RMT | 1158300
7 | 2700 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 204.1 | M | 551070
8 | 20 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) -33 KV 3x400 Sqmm Cable | Elect | Labour | SWR12004 | 323.85 | M | 6477
9 | 34 | Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs - In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-33 KV 3x400 Sqmm Cable-SR | Elect | Labour | SWR11918 | 572.1 | M | 19451.4
10 | 26 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-33 KV 3x400 Sqmm Cable-SR | Elect | Labour | SWR11954 | 135.66 | M | 3527.16
11 | 10 | Making of Outdoor/Indoor End Termination-33KV 3x400 Sqmm Cable | Elect | Labour | SWR10387 | 2764.76 | EA | 27647.6
12 | 30 | Making of Straight through joints-33KV 3x400 Sqmm Cable | Elect | Labour | SWR10382 | 5700.78 | EA | 171023.4
13 | 1600 | Supply of 6" B class GI pipe | Elect | Supply | SMR40081 | 1044 | M | 1670400
14 | 2700 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 81000
15 | 25 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 68625
16 | 1 | Submission of auto CAD Drawing as per pole schedule (Detailed survey and sketch)-Up to 10km | Elect | Labour | SWR12104 | 6000 | LS | 6000
17 | 30 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 14520
18 | 1 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 4500
19 | 1 | Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10239 | 126 | EA | 126
20 | 1 | Un loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10557 | 79 | EA | 79
21 | 100 | supply of 6" DWC pipe | Elect | Supply | SMR11610 | 1012 | M | 101200
22 | 120 | CartAway Debris from Ofc Pre to Dumpyard | Elect | Labour | SWR34266 | 1038 | EA | 124560
23 | 6 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 3075.3
24 | 3 | Excavation of pits in all soils except hard rock requiring blasting-11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M (1.31 cum) | Elect | Labour | SWR10108 | 629.85 | EA | 1889.55
25 | 2 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 5287.66
26 | 6 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 456
27 | 6 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 300
28 | 6 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 6792
29 | 0.27 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Elect | Labour | SWR10206 | 221 | TO | 59.67
30 | 0.27 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Elect | Labour | SWR10524 | 185 | TO | 49.95
31 | 1.59 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading )-Above 10 KM and upto 20 KM | Elect | Labour | SWR10132 | 412.08 | TO | 655.2072
32 | 2.64 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 17368.56
33 | 0.093 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3893.01 | M3 | 362.0499
34 | 3 | Painting of coping with two coats of white cement including cost of paint & conveyance charges for PTR/VCB plinths | Elect | Labour | SWR12334 | 160 | EA | 480
35 | 2 | Supply of earthing pipe with materials Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specification | Elect | Supply | SMR11482 | 3486 | EA | 6972
36 | 2 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wireetc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 2468.4
37 | 2 | Providing of RCC Collar guarding to the existing earth pits withdamaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 772
38 | 1 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 142
39 | 3 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 159
40 | 50 | Supply of earthing pipe with materials Supply of GI Flat 25X3 mm | Elect | Supply | SMR11485 | 105 | KG | 5250
41 | 50 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 5875
42 | 0.27 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 588.87
43 | 0.27 | Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 229.77
44 | 0.27 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 349.11
45 | 0.27 | Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elect | Labour | SWR10879 | 482 | TO | 130.14
46 | 50 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc.-M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Elect | Labour | SWR10919 | 41 | RMT | 2050
47 | 1 | Erection of 33kv LA-3Nos Line type | Elect | Labour | SWR20976 | 880 | SET | 880
48 | 3 | Supply of Alluminum LA clamps conforming to A6 of IS 617,with hot dip galvanised bolts and nuts suitable for single zebra /Panther | Elect | Supply | SMR40027 | 357 | EA | 1071
49 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Erection of 5 Mts RS Joist (Bit) Pole including fixing of Pole Mounted Box | Elect | Labour | SWR20863 | 1044.23 | EA | 1044.23
50 | 1 | Loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10198 | 1024 | EA | 1024
51 | 1 | Un loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10516 | 1044.48 | EA | 1044.48
52 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)- Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
53 | 1 | Erection of 33 KV VCB with Control Panel | Elect | Labour | SWR10460 | 12500 | EA | 12500
54 | 1 | Erection of 33 KV CTs | Elect | Labour | SWR10399 | 1079 | SET | 1079
55 | 4.8 | Excavate-Pit for 33KV VCB | Elect | Labour | SWR23224 | 331 | M3 | 1588.8
56 | 6 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | Elect | Labour | SWR20685 | 5160 | M3 | 30960
57 | 6.4 | Plastering 2 Coats,20/16mm(1:6)(1:4) | Elect | Labour | SWR10862 | 373 | M2 | 2387.2
58 | 1 | Painting of coping with two coats of white cement including cost of paint & conveyance charges for PTR/VCB plinths | Elect | Labour | SWR12334 | 160 | EA | 160
59 | 2 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 9000
60 | 2 | Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10239 | 126 | EA | 252
61 | 2 | Un loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10557 | 79 | EA | 158
62 | 2 | Yard lightning-Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79kgf as per IS 2713 | Elect | Supply | SMR40051 | 13913 | EA | 27826
63 | 2 | Erection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 2758
64 | 2 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE /CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE:PHILIPS LUMILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor,Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency,minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty-90W LED Fixture set | Elect | Supply | SMR11594 | 8200 | EA | 16400
65 | 2 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Elect | Labour | SWR10956 | 1268 | EA | 2536
66 | 14 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable | Elect | Labour | SWR10642 | 512.55 | EA | 7175.7
67 | 7 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 18506.81
68 | 2 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Erection of 5 Mts RS Joist (Bit) Pole including fixing of Pole Mounted Box | Elect | Labour | SWR20863 | 1044.23 | EA | 2088.46
69 | 16 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1216
70 | 16 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 800
71 | 16 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 18112
72 | 8.43 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 55460.97
73 | 9 | Excavation of pits in all soils except hard rock requiring blasting-11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M (1.31 cum) | Elect | Labour | SWR10108 | 629.85 | EA | 5668.65
74 | 0.279 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3893.01 | M3 | 1086.1498
75 | 9 | Painting of coping with two coats of white cement including cost of paint & conveyance charges for PTR/VCB plinths | Elect | Labour | SWR12334 | 160 | EA | 1440
76 | 3 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elect | Supply | SMR11482 | 3486 | EA | 10458
77 | 3 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wireetc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 3702.6
78 | 3 | Providing of RCC Collar guarding to the existing earth pits withdamaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 1158
79 | 3 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 426
80 | 6 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 318
81 | 2 | Dismantling of Damaged Poles, not required and available in the middle of roads, transporting to stock point etc.-Dism of Box pole 9/10/11 Mtr | Elect | Labour | SWR11329 | 1130 | EA | 2260
82 | 2 | Dismantling of Damaged Poles, not required and available in the middle of roads, transporting to stock point etc.-Dism of RS Joists 175 x 85 Mm | Elect | Labour | SWR11324 | 1116 | EA | 2232
83 | 1 | Dismantling of all types of 33 kV AB switches | Elect | Labour | SWR11743 | 1281.38 | EA | 1281.38
84 | 1 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 4500
85 | 1.25 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Elect | Labour | SWR10206 | 221 | TO | 276.25
86 | 1.25 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Elect | Labour | SWR10524 | 185 | TO | 231.25
87 | 4.89 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading )-Above 10 KM and upto 20 KM | Elect | Labour | SWR10132 | 412.08 | TO | 2015.0712
88 | 6 | Supply of Tension Hardware 3 Bolted for single Zebra/pantherwith 150 mm spacing. | Elect | Supply | SMR11915 | 2055 | SET | 12330
89 | 1 | Supply of AC Supply panel complete | Elect | Supply | SMR11630 | 27000 | EA | 27000
90 | 1 | Fixing of AC Supply panel complete | Elect | Labour | SWR11825 | 5000 | EA | 5000
91 | 6 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | Elect | Labour | SWR10404 | 327.68 | M | 1966.08
92 | 3 | Supply of I hook | Elect | Supply | SMR12099 | 158 | EA | 474
93 | 3 | Erection of I hook | Elect | Labour | SWR12099 | 55 | EA | 165
94 | 145.8 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc.-M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Elect | Labour | SWR10919 | 41 | RMT | 5977.8
95 | 100 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 11750
96 | 32 | Cutting charges for MS Sections-MS Channel 100 x 50 mm | Elect | Labour | SWR10294 | 10 | EA | 320
97 | 1.25 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 2726.25
98 | 1.25 | Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 1063.75
99 | 1.25 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 1616.25
100 | 1.25 | Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elect | Labour | SWR10879 | 482 | TO | 602.5
101 | 4.54 | Alligning the Main and Auxiliary structures such as RS joist,M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Elect | Labour | SWR10867 | 1470 | TO | 6673.8
102 | 1 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt) | Elect | Labour | SWR21240 | 781 | EA | 781
103 | 6 | Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Elect | Labour | SWR10884 | 224 | EA | 1344
104 | 40 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Elect | Labour | SWR12510 | 27 | EA | 1080
105 | 3 | Supply of Alluminum LA clamps conforming to A6 of IS 617, with hot dip galvanised bolts and nuts suitable for single zebra /Panther | Elect | Supply | SMR40027 | 357 | EA | 1071
106 | 6 | Supply of CT stud clamps with hot dip galvanised bolts and nuts suitable for zebra / Panther conductor on one side and 28/30/40 mm CT stud on other side with stud size for single zebra / panther (4 bolted) with bimetallic sleeve for carrying 800 A | Elect | Supply | SMR40023 | 399 | EA | 2394
107 | 1 | Erection of 33kv LA-3Nos Line type | Elect | Labour | SWR20976 | 880 | SET | 880
108 | 150 | Cut-Tree Branch(LT/11/33)&Trnsprt Debris | Elect | Labour | SWR23200 | 4 | EA | 600
109 | 400 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends | Elect | Labour | SWR11879 | 27 | M | 10800
| Sub Total: | [6 empty] | 7154380.8281
| 18% Service tax on labour | [6 empty] | 1287788.5491
| Total Rs. | [6 empty] | 8442169.3772
8029167.14
413002.24
|  | 350001.9 |  | 6804378.93 |  | 8442169.38
|  | 63000.34 |  | 1224788.2074
8029167.1374
413002.24
7154380.83
|  |  |  | 1287788.5474 |  |  | -0.0002184
8442169.3774
8442169.3774
0