## Schedule
SCHEDULE
Name of the work: Erection of new 33/11kV Outdoor SS with 2X8 MVA PTRs and 8 Nos. 11kV Feeders at JonnaBanda SS alongwith Construction of control room, RCC Retaining wall, Compound Wall, Switch yard, PTR Plinths, Rock cutting , Gravel filling, Drilling of Borewell and other miscellaneous civil works .
WBS No: S-1660-12-01-02-01-001 (Electrical) & S-1660-12-07-01-01-001 (Civil)
SNo | S No. | EstimatE Quantity (only FigurEs) | Item DEtailEd SpEcification Description | Work Type | Item Short Descripti | Service Code | Rate | UOM | Amount
Electrical Portion
| 1 | 8 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elect | Supply | SMR11482 | 3486 | EA | 27888
| 2 | 8 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 9873.6
| 3 | 1 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 1024
| 4 | 1 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 1024
| 5 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
| 6 | 115 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,-Along the CC / BT multi layer road requiring compressor-11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11981 | 1264.64 | M | 145433.6
| 7 | 20 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil/CC-11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11973 | 631.06 | M | 12621.2
| 8 | 135 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 204.1 | M | 27553.5
| 9 | 5 | Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | Elect | Labour | SWR10391 | 2370.63 | EA | 11853.15
| 10 | 0.25 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel,iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading )-Above 10 KM and upto 20 KM | Elect | Labour | SWR10132 | 412.08 | TO | 103.02
| 11 | 2 | Supply of Danger boards with clamps | Elect | Supply | SMR40070 | 116 | EA | 232
| 12 | 1 | Geophysical Investgation Charges | Elect | Labour | SWR33608 | 5000 | EA | 5000
| 13 | 300 | Drill-165mm Bore Well 270M and above | Elect | Labour | SWR34836 | 1082 | M | 324600
| 14 | 35 | S&F 160mm dia PVC Casing | Elect | Labour | SWR33611 | 883 | M | 30905
| 15 | 1.5 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel,iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading )-Above 10 KM and upto 20 KM | Elect | Labour | SWR10132 | 412.08 | TO | 618.12
| 16 | 8 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elect | Labour | SWR10359 | 386 | EA | 3088
| 17 | 270 | Supply of 4" B class GI pipe | Elect | Supply | SMR40080 | 740 | M | 199800
| 18 | 372.34 | Laying of earth mat including excavation of trenches of depth 600mm, welding,connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication.-75x 8mm MS Flat / GI Flat. | Elect | Labour | SWR10920 | 65 | RMT | 24202.1
| 19 | 1.75 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Elect | Labour | SWR10206 | 221 | TO | 386.75
| 20 | 1.75 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Elect | Labour | SWR10524 | 185 | TO | 323.75
| 21 | 1 | Supply & Erection of SP SubMrsbl Pumpset | Elect | Labour | SWR33640 | 48007 | EA | 48007
| 22 | 16 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | Elect | Supply | SMR40051 | 13913 | EA | 222608
| 23 | 16 | Erection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 22064
| 24 | 16 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE /CROMPTON/ BAJAJ/VIN/ WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE /NICHIA/OSRAM/ SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing,toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty-90W LED Fixture set | Elect | Supply | SMR11594 | 8200 | EA | 131200
| 25 | 16 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Elect | Labour | SWR10956 | 1268 | EA | 20288
| 26 | 52 | Excavation of pits in hard rock requiring blasting. (other than SS)-9.1Mtrs PSCC Pole 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elect | Labour | SWR10112 | 1770 | EA | 92040
| 27 | 52 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | Elect | Labour | SWR10348 | 1952.61 | EA | 101535.72
| 28 | 52 | Loading of R.S. Joists 150 x 150mm / Rail poles | Elect | Labour | SWR10205 | 176 | EA | 9152
| 29 | 52 | Un-Loading of R.S. Joists 150 x 150mm / Rail poles | Elect | Labour | SWR10523 | 107 | EA | 5564
| 30 | 52 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 58864
| 31 | 17.5 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Elect | Labour | SWR10206 | 221 | TO | 3867.5
| 32 | 17.5 | Un Loading of M.S.Channels, Angles, Flats & Rods etc., | Elect | Labour | SWR10524 | 185 | TO | 3237.5
| 33 | 36.22 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel,iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading )-Above 10 KM and upto 20 KM | Elect | Labour | SWR10132 | 412.08 | TO | 14925.5376
| 34 | 68.44 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 450266.76
| 35 | 60.008 | Plastering 2 Coats,20/16mm(1:6)(1:4) | Elect | Labour | SWR10862 | 373 | M2 | 22382.984
| 36 | 8.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.-Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 18538.5
| 37 | 8.5 | Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 7233.5
| 38 | 52 | Painting suppports of 0.3m with bitumen | Elect | Labour | SWR10880 | 688 | EA | 35776
| 39 | 8 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-8.0 m long PSCC pole | Elect | Labour | SWR10342 | 1500 | EA | 12000
| 40 | 500 | Supply of rail poles 90/105lb (250x2N) | Elect | Supply | SMR22718 | 47.27 | KG | 23635
| 41 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Rail pole 90 lbs | Elect | Labour | SWR10344 | 3510 | EA | 14040
| 42 | 20 | Laying of XLPE UG Single Run cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil / CC/BT Road-33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11918 | 572.1 | M | 11442
| 43 | 27.72 | Alligning the Main and Auxiliary structures such as RS joist,M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Elect | Labour | SWR10867 | 1470 | TO | 40748.4
| 44 | 27.72 | Fabrication of Main and Auxiliary structures with power drillingusing raw steel such as M.S.Angles, Plates, Channels,R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site,including erection. | Elect | Labour | SWR10868 | 6852 | TO | 189937.44
| 45 | 27.72 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.-Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 60457.32
| 46 | 27.72 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.-Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium | Elect | Labour | SWR10879 | 482 | TO | 13361.04
| 47 | 27.72 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete-Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 35841.96
| 48 | 27.72 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete-Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 23589.72
| 49 | 500 | Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions | Elect | Labour | SWR10873 | 83 | KG | 41500
| 50 | 42 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | Elect | Supply | SMR11915 | 2055 | SET | 86310
| 51 | 8 | Supply of Tension clamps for earth wire 3 bolted (Bus Stringing) | Elect | Supply | SMR40017 | 715 | SET | 5720
| 52 | 24 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts &Bolts includng spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961)-Supply of I Bolts | Elect | Supply | SMR22473 | 294 | EA | 7056
| 53 | 90 | Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nutswith spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . | Elect | Supply | SMR40011 | 299 | EA | 26910
| 54 | 60 | Supply of CT stud clamps with hot dip galvanised bolts and nuts suitable for zebra / Panther conductor on one side and 28/30/40 mm CT stud on other side with stud size for single zebra / panther (4 bolted) with bimetallic sleeve for carrying 800 A | Elect | Supply | SMR40023 | 399 | EA | 23940
| 55 | 31 | Supply of Alluminum alloy Pad clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for twin panther ACSR/Zebra of pad size 100 X 100 X15mm for carrying 1200 A current rating . | Elect | Supply | SMR40021 | 284 | EA | 8804
| 56 | 12 | Supply of Alluminum PT clamps conforming to A6 of IS 617,with hot dip galvanised bolts and nuts suitable for single zebra/ Panther | Elect | Supply | SMR40025 | 368 | EA | 4416
| 57 | 36 | Supply of Alluminum LA clamps conforming to A6 of IS 617, with hot dip galvanised bolts and nuts suitable for single zebra / Panther | Elect | Supply | SMR40027 | 357 | EA | 12852
| 58 | 9 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt) | Elect | Labour | SWR21240 | 781 | EA | 7029
| 59 | 12 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Elect | Labour | SWR21241 | 507 | EA | 6084
| 60 | 60 | Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Elect | Labour | SWR10884 | 224 | EA | 13440
| 61 | 133.3 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | Elect | Labour | SWR10404 | 327.68 | M | 43679.744
| 62 | 303 | Labour for Fixing of all types of clamps | Elect | Labour | SWR10917 | 65 | EA | 19695
| 63 | 13 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 58500
| 64 | 21 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR10393 | 3200 | EA | 67200
| 65 | 1 | Erection of control/Relay panels, AC Panels, announciation panels etc in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Elect | Labour | SWR11893 | 2122 | EA | 2122
| 66 | 35 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.-Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 4970
| 67 | 64.584 | Excavate-Pit for 33KV VCB | Elect | Labour | SWR23224 | 331 | M3 | 21377.304
| 68 | 74.52 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x1.8 x 0.75 cum for VCB Plinth | Elect | Labour | SWR20685 | 5160 | M3 | 384523.2
| 69 | 2 | Erection of 33 KV VCB with Control Panel | Elect | Labour | SWR10460 | 12500 | EA | 25000
| 70 | 10 | Erection of 11 KV VCB with Control Panel | Elect | Labour | SWR10461 | 12000 | EA | 120000
| 71 | 16 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M(2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | EA | 14848
| 72 | 4 | Supply of Copper Flexible jumper with 75 X 8 of length 250mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral | Elect | Supply | SMR40033 | 4725 | EA | 18900
| 73 | 12 | Supply of Bimetalic Copper die clamps suitable for power transformer/ Lclamps HV of 1/2 inch bush rod and other end suitable for panther conductor and with bimetallic sheet on the pad of size 75X75X10mm with four holes of 14mm diameter (hole to hole distance 40mm) with suitable GI bolts and nuts including washers | Elect | Supply | SMR40039 | 909 | EA | 10908
| 74 | 4 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | SET | 3520
| 75 | 2 | Erection of 11 KV LAS station type including earthing | Elect | Labour | SWR10397 | 559 | SET | 1118
| 76 | 8 | Erection of 11 KV LAS line type including earthing | Elect | Labour | SWR10398 | 505 | SET | 4040
| 77 | 34 | Providing of earthing with various types of earth electrodes-Supply of copper bonded steel rod of dia 5/8 inch with a length of 3meters, suitable for connecting 75X8 MS strip and supply of 33.9kgs ground enhancing meterial GEM-25A /Zerolyte of 0.2 ohm meter resistiviity as per IEE 142-1991 for 33/11kV Sub-Station | Elect | Supply | SMR40042 | 8820 | EA | 299880
| 78 | 34 | Installation of copper bonded steel rod of dia 5/8 inch with a length of 3meters refilling with ground enhancing meterial EM- 25A / Zerolyte of 0.2 ohm meter resistiviity IEE 142-1992 in Hard Rock with bore 10"dia & 20feet deep or trench of 4'W X10'L X 5' depth back filled with black cotton soil | Elect | Labour | SWR10928 | 8004 | EA | 272136
| 79 | 34 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elect | Labour | SWR10359 | 386 | EA | 13124
| 80 | 1800 | Fabrication and connecting to risers from earth mat to structures, equipment,marshalling boxes, electrical panels, PLCC panels, fencing posts etc-M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Elect | Labour | SWR10919 | 41 | RMT | 73800
| 81 | 957.45 | Laying of earth mat including excavation of trenches of depth 600mm, welding,connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication.-75x 8mm MS Flat / GI Flat. | Elect | Labour | SWR10920 | 65 | RMT | 62234.25
| 82 | 2500 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends | Elect | Labour | SWR11879 | 27 | M | 67500
| 83 | 270 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Elect | Labour | SWR12510 | 27 | EA | 7290
| 84 | 1 | Erection of 220 V, 80 AH battery in complete shape fit for charging . VRLA(maintenance free) | Elect | Labour | SWR12344 | 2783 | EA | 2783
| 85 | 1 | Erection of 220 V, 80 AH battery charger with Distribution board. | Elect | Labour | SWR12346 | 2783 | EA | 2783
| 86 | 1 | Loading of 220V Battery set | Elect | Labour | SWR12083 | 900 | EA | 900
| 87 | 1 | Un-Loading of 220V Battery set | Elect | Labour | SWR12084 | 900 | EA | 900
| 88 | 1 | Loading of 220V Charger | Elect | Labour | SWR11244 | 572 | EA | 572
| 89 | 1 | Un-Loading of 220V Charger | Elect | Labour | SWR11245 | 366 | EA | 366
| 90 | 90 | Providing of control cable trench as per DATA-XII | Elect | Labour | SWR22093 | 3148 | RMT | 283320
| 91 | 1 | Construction of DTR Plinth- RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | Elect | Labour | SWR21843 | 25967.57 | EA | 25967.57
| 92 | 1 | Loading of 50,63, 75 & 100 KVA DTR | Elect | Labour | SWR10195 | 350 | EA | 350
| 93 | 1 | Un-Loading of 50,63, 75 & 100 KVA DTR | Elect | Labour | SWR10513 | 280 | EA | 280
| 94 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc-Erection of 3 Ph DTRs upto 25KVA | Elect | Labour | SWR10463 | 1139.95 | EA | 1139.95
| 95 | 30 | Laying of XLPE UG Single Run cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable,placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil / CC/BT Road-11KV 3x185 Sqmm Cable | Elect | Labour | SWR11920 | 465.46 | M | 13963.8
| 96 | 20 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x185 Sqmm Cable | Elect | Labour | SWR11956 | 126.23 | M | 2524.6
| 97 | 2 | Making 11 KV 3x185 Sqmm Cable Out Door/Indoor end termination | Elect | Labour | SWR10390 | 2370.63 | EA | 4741.26
| 98 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Elect | Labour | SWR10674 | 1594.67 | EA | 1594.67
| 99 | 1 | Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification. | Elect | Supply | SMR40044 | 42500 | EA | 42500
| 100 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. | Elect | Supply | SMR40045 | 42000 | EA | 42000
| 101 | 2 | Fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supply | Elect | Labour | SWR20025 | 7871.85 | SET | 15743.7
| 102 | 3 | Supply of FRP PT Marshalling Box | Elect | Supply | SMR40048 | 4463 | EA | 13389
| 103 | 3 | Erection of Marshalling boxes | Elect | Labour | SWR10940 | 374.85 | EA | 1124.55
| 104 | 2 | Erection of 33 KV single phase PTs | Elect | Labour | SWR10401 | 1079 | SET | 2158
| 105 | 2 | Erection of 11 KV three phase PTs | Elect | Labour | SWR10402 | 800 | SET | 1600
| 106 | 12 | Wirring, commissioning and testing of Outdoor Sub-station switchgear duly conducting the pre commissioning test as per relevent standards & issue of certificate by CEIG authorised testing Engineer | Elect | Labour | SWR10942 | 1825 | EA | 21900
| 107 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading )-8MVA power transformer | Elect | Labour | SWR10854 | 21945 | EA | 43890
| 108 | 2 | Loading of 8MVA PTR | Elect | Labour | SWR10613 | 5805.84 | EA | 11611.68
| 109 | 2 | Un-Loading of 8MVA PTR | Elect | Labour | SWR10627 | 5805.84 | EA | 11611.68
| 110 | 2 | Erection of PTR on constructed plinth-Erection of 8 MVA PTR. | Elect | Labour | SWR21321 | 49480.2 | EA | 98960.4
| 111 | 2 | Testing of Power Transformer duly conducting the pre commissioning tests as per relevent standard & issue of certificate by CEIG authorised testing Engineer | Elect | Labour | SWR10944 | 4000 | EA | 8000
| 112 | 2 | Loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10198 | 1024 | EA | 2048
| 113 | 2 | Un-Loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10516 | 1044.48 | EA | 2088.96
| 114 | 10 | Loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10199 | 1024 | EA | 10240
| 115 | 10 | Un-Loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10517 | 1044.48 | EA | 10444.8
| 116 | 75 | Supply of earthing pipe with materials GI Flat 25X3 mm | Elect | Supply | SMR11485 | 105 | KG | 7875
| 117 | 90 | Laying of XLPE UG Single Run cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable,placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.- In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil / CC/BT Road-LT 3 1/2 x 185 Sqmm Cable | Elect | Labour | SWR11923 | 377.63 | M | 33986.7
| 118 | 10 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-LT 3 1/2 x 185 Sqmm Cable | Elect | Labour | SWR11959 | 85.43 | M | 854.3
| 119 | 2 | Supply of 31/2x185Sqmm UG O/D end termination kits Making of Outdoor/Indoor End Termination | Elect | Supply | SMR40140 | 550 | EA | 1100
| 120 | 1 | Loading of 11 KV HG Fuse Sets | Elect | Labour | SWR10231 | 18 | EA | 18
| 121 | 1 | Un Loading of 11 KV HG Fuse Sets | Elect | Labour | SWR10549 | 18 | EA | 18
| 122 | 1 | Erection of 11 KV HG Fuse set including earthing | Elect | Labour | SWR10395 | 740.52 | SET | 740.52
| 123 | 2 | Supply & fixing of Oout Door/Indoor end termination LT 3 1/2 x185 Sqmm Cable | Elect | Labour | SWR10765 | 968.9 | EA | 1937.8
| 124 | 1 | Loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10238 | 80 | EA | 80
| 125 | 1 | Un Loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10556 | 80 | EA | 80
| 126 | 1 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR20102 | 1813.49 | EA | 1813.49
| 127 | 3 | Supply of 11kv, 200Amps copper Flexible jumpers | Elect | Supply | SMR40032 | 131 | EA | 393
| 128 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard | Elect | Labour | SWR20032 | 1654 | EA | 1654
| 129 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Elect | Labour | SWR22090 | 2205 | EA | 2205
| 130 | 1 | T & P - Supply of -Wall clock standard make | Elect | Supply | SMR40059 | 578 | EA | 578
| 131 | 1 | Supply of Angle racks(18x36.6inches) Godrej | Elect | Supply | SMR40060 | 1733 | EA | 1733
| 132 | 1 | Supply of 10ft Aluminium Ladder | Elect | Supply | SMR12378 | 1654 | EA | 1654
| 133 | 30 | Painting of Name Plates for any equipment | Elect | Labour | SWR10963 | 122 | EA | 3660
| 134 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7,8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19,20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378- 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579- 1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. | Elect | Supply | SMR40063 | 4925 | SET | 4925
| 135 | 1 | Supply of Rechargeable LED torch light of Standard make | Elect | Supply | SMR40064 | 1733 | EA | 1733
| 136 | 1 | Supply of Steel almarah(61/2 X 3ft) Godrej | Elect | Supply | SMR40061 | 9818 | EA | 9818
| 137 | 1 | Supply of Table (3x6ft) Godrej | Elect | Supply | SMR40057 | 6050 | EA | 6050
| 138 | 4 | Supply of S type chairs (Godrej) | Elect | Supply | SMR40058 | 924 | EA | 3696
| 139 | 1 | Supply of Hack saw (12 inches) | Elect | Supply | SMR40065 | 289 | EA | 289
| 140 | 4 | Supply of Earth Rods (8ft) Screw & clamp type | Elect | Supply | SMR40066 | 578 | EA | 2312
| 141 | 2 | Supply of Hand Gloves | Elect | Supply | SMR40067 | 289 | SET | 578
| 142 | 15 | Supply of Rubber mats ( 6’x3’) size for indoor SS | Elect | Supply | SMR40068 | 1386 | EA | 20790
| 143 | 1 | Supply of Standard basic cell phone with charger | Elect | Supply | SMR40069 | 1386 | EA | 1386
| 144 | 14 | Supply of Danger boards with clamps | Elect | Supply | SMR40070 | 116 | EA | 1624
| 145 | 1 | Supply of Fire bucket stand with 3 buckets (8 -10 ltr capacity) | Elect | Supply | SMR40088 | 1386 | SET | 1386
| 146 | 2 | Supply of Room fire extinguisher (2 ltrs capacity) for control room | Elect | Supply | SMR40089 | 4620 | EA | 9240
| 147 | 4 | Supply of Trolley mounted CO2 (6.5Kgs) | Elect | Supply | SMR40087 | 9240 | EA | 36960
| 148 | 6 | Supply of Safety Helmets of standard make | Elect | Supply | SMR40071 | 231 | EA | 1386
| 149 | 8 | Supply of LC Boards | Elect | Supply | SMR40072 | 116 | EA | 928
| 150 | 4 | Supply of Gum Boots (Pair) | Elect | Supply | SMR40073 | 693 | EA | 2772
| 151 | 1 | Supply of 5000v megger | Elect | Supply | SMR40074 | 13860 | EA | 13860
| 152 | 1 | Supply of Earth megger (1000v) | Elect | Supply | SMR40075 | 8085 | EA | 8085
| 153 | 1 | Supply of Digital clamp meter | Elect | Supply | SMR40076 | 2888 | EA | 2888
| 154 | 1 | Supply of Name board of the 33/11kV Sub-Station(As per Standard Specification) | Elect | Supply | SMR40086 | 10238 | EA | 10238
| 155 | 0.1 | Supply of Extention of 33KV Bay at 132/33KV Sub-station-Zebra condutor | Elect | Supply | SMR24910 | 299369 | KM | 29936.9
| 156 | 8 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)-8 Mtrs long PSCC Poles | Elect | Labour | SWR20307 | 271.52 | EA | 2172.16
| 157 | 7.04 | Earth work excavation of in all soils except hard rock requiring blasting. | Elect | Labour | SWR20768 | 345 | M3 | 2428.8
| 158 | 7.04 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 46316.16
| 159 | 6 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 19798.2
| 160 | 13 | Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10239 | 126 | EA | 1638
| 161 | 13 | Un Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10557 | 79 | EA | 1027
| 162 | 21 | Loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10238 | 80 | EA | 1680
| 163 | 21 | Un Loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10556 | 80 | EA | 1680
| 164 | 2.604 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 10137.372
| 165 | 35 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 5132.05
| 166 | 16.912 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. | Elect | Labour | SWR10356 | 6579 | M3 | 111264.048
| 167 | 6 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 6144
| 168 | 6 | Un Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 6144
| 169 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 13198.8
| 170 | 400 | Laying of XLPE UG cable Triple or more Run including excavation of trench of size 1000mm wide to 750mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs &33 KV - 1.20 mtrs.Along the CC / BT multi layer road requiring compressor-33 KV 3x400 Sqmm Cable | Elect | Labour | SWR12019 | 1731.45 | M | 692580
| 171 | 100 | Laying of XLPE UG cable Triple or more Run including excavation of trench of size 1000mm wide to 750mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs &33 KV - 1.20 mtrs.Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe)-33 KV 3x400 Sqmm Cable | Elect | Labour | SWR12024 | 1978.8 | M | 197880
| 172 | 1000 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 204.1 | M | 204100
| 173 | 150 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11954 | 135.66 | M | 20349
| 174 | 14 | Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination | Elect | Labour | SWR10387 | 2764.76 | EA | 38706.64
| 175 | 6 | Making of Straight through joints-33 KV 3x400 Sqmm Cable | Elect | Labour | SWR10382 | 5700.78 | EA | 34204.68
| 176 | 50 | Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | Elect | Supply | SMR40077 | 363 | M | 18150
| 177 | 970 | Supply of 6" B class GI pipe Cost of Pipes and slabs | Elect | Supply | SMR40081 | 1044 | M | 1012680
| 178 | 50 | supply of 6" DWC pipe Cost of Pipes and slabs | Elect | Supply | SMR11610 | 1012 | M | 50600
| 179 | 500 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours.-11KV | Elect | Labour | SWR21903 | 30 | M | 15000
| 180 | 2 | Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10239 | 126 | EA | 252
| 181 | 2 | Un Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10557 | 79 | EA | 158
| 182 | 2 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 9000
| 183 | 3 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elect | Supply | SMR11482 | 3486 | EA | 10458
| 184 | 3 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 3702.6
| 185 | 3 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elect | Labour | SWR10359 | 386 | EA | 1158
| 186 | 2 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 293.26
| 187 | 0.186 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3893.01 | M3 | 724.0999
| 188 | 12 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 6150.6
| 189 | 6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 15862.98
| 190 | 12 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 912
| 191 | 12 | Un-Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 600
| 192 | 6 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 6792
| 193 | 6.3 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 41447.7
| 194 | 6 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | Elect | Labour | SWR10107 | 700 | EA | 4200
| 195 | 7.17 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Elect | Labour | SWR10206 | 221 | TO | 1584.57
| 196 | 7.17 | Un Loading of M.S.Channels, Angles, Flats & Rods etc., | Elect | Labour | SWR10524 | 185 | TO | 1326.45
| 197 | 10.17 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel,iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading )-Above 10 KM and upto 20 KM | Elect | Labour | SWR10132 | 412.08 | TO | 4190.8536
| 198 | 30 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)-Trans 11/12.5/12.9M Spun pole upto 50KM | Elect | Labour | SWR11181 | 858 | EA | 25740
| 199 | 30 | Loading of Spun poles 12.5 M | Elect | Labour | SWR10190 | 548 | EA | 16440
| 200 | 30 | Un loading of Spun poles 12.5 M | Elect | Labour | SWR10508 | 363 | EA | 10890
| 201 | 30 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Spun poles 12.5 Mtrs / 12.9Mtrs PSCC | Elect | Labour | SWR10350 | 4521.66 | EA | 135649.8
| 202 | 15 | Excavation of pits in all soils except hard rock requiring blasting-12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") 1.94 cum | Elect | Labour | SWR10109 | 842.78 | EA | 12641.7
| 203 | 15 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") | Elect | Labour | SWR11041 | 1466.25 | EA | 21993.75
| 204 | 58.4 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 384213.6
| 205 | 6 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 16470
| 206 | 1 | Submission of auto CAD Drawing as per pole schedule (Detailed survey and sketch)-Up to 10 km | Elect | Labour | SWR12104 | 6000 | LS | 6000
| 207 | 1.2 | Paving out and stringing of conductor by providing temporary stays, tensioning,sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-100 Sqmm Double Circuit (6 Conductors). | Elect | Labour | SWR10704 | 26255.98 | KM | 31507.176
| 208 | 5 | Formation of Cut point for 33 KV Double circuit line excluding pole erection and stays | Elect | Labour | SWR10466 | 3198.72 | EA | 15993.6
| 209 | 1.2 | Dismantling of 11KV 34/55 sqmm SC | Elect | Labour | SWR22065 | 4500 | KM | 5400
| 210 | 1.2 | Restringing of existing loose Lines by removing the pin-binding and jumpers, Providing of temporary stays, providing stiffners pieces, replacement of damaged insulators, alignment of cross arms, pin binding and jumpering after tensioning and removing of the temporary stays complete-33/11 KV lines-Restringing of with 55 Sqmm single ckt 3 cond | Elect | Labour | SWR11308 | 6616 | KM | 7939.2
| 211 | 1.2 | Restringing of existing loose Lines by removing the pin-binding and jumpers, Providing of temporary stays, providing stiffners pieces, replacement of damaged insulators, alignment of cross arms, pin binding and jumpering after tensioning and removing of the temporary stays complete-LT lines :-Restring. Of LT line 4w/l with 34 Sqmm | Elect | Labour | SWR11313 | 7270 | KM | 8724
| 212 | 2 | Loading of Conductor drums | Elect | Labour | SWR10191 | 202 | EA | 404
| 213 | 2 | Un Loading of Conductor drums | Elect | Labour | SWR10509 | 100 | EA | 200
| 214 | 150 | Loading of 33 & 11 KV Disc insulators | Elect | Labour | SWR12416 | 2 | CRT | 300
| 215 | 150 | Un loading of 33 KV Pin insulators | Elect | Labour | SWR10529 | 3 | CRT | 450
| 216 | 60 | Loading of 33 & 11 KV Disc insulators | Elect | Labour | SWR12416 | 2 | CRT | 120
| 217 | 60 | Un Loading of 33 & 11 KV Disc insulators | Elect | Labour | SWR10631 | 2 | CRT | 120
| 218 | 3 | Loading of 33 KV Metal parts | Elect | Labour | SWR10618 | 65 | BAG | 195
| 219 | 3 | Un Loading of 33 KV Metal parts | Elect | Labour | SWR10632 | 65 | BAG | 195
| 220 | 75 | Supply of earthing pipe with materials-Supply of GI wire No 8 | Elect | Supply | SMR11486 | 105 | KG | 7875
| 221 | 5 | Earthing of Sub-Station- Supply of GI pipe 40 mm dia, 2 mtrs, 3mm thickness with bolts and nuts | Elect | Supply | SMR40091 | 733 | EA | 3665
| 222 | 5 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 6171
| 223 | 7000 | Cut-Tree Branch(LT/11/33)&Trnsprt Debris | Elect | Labour | SWR23200 | 4 | EA | 28000
| 224 | 1750 | Supply of earthing pipe with materials-Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 205625
| 225 | 10 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 4840
| 226 | 150 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Elect | Labour | SWR11879 | 27 | M | 4050
| 227 | 12 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properlyramming including transport of materials from road side to location excluding pit excavation-11 Mtrs PSCC poles | Elect | Labour | SWR10978 | 4336.85 | EA | 52042.2
| 228 | 12 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)-11 Mtrs long PSCC Poles | Elect | Labour | SWR11180 | 431.97 | EA | 5183.64
| 229 | 12 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | Elect | Labour | SWR10107 | 700 | EA | 8400
| 230 | 15.79 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 103882.41
| 231 | 3 | Supply of M+3 Tower (Galvanized) | Elect | Supply | SMR11683 | 140674.3 | EA | 422022.9
| 232 | 3 | Erection of M+3 Tower (Galvanized) | Elect | Labour | SWR11850 | 64576 | EA | 193728
| 233 | 6 | Supply of material for Extension of 3Mtrs for M+3 (Galvanized) | Elect | Supply | SMR11684 | 28520.64 | EA | 171123.84
| 234 | 6 | Erection of Extension of 3Mtrs for M+3 (Galvanized) | Elect | Labour | SWR11851 | 5168.95 | EA | 31013.7
| 235 | 14.256 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-M-Type Tower (1.2M x 1.2M x 3.3M ) 4.752cum | Elect | Labour | SWR12090 | 3592.95 | EA | 51221.0952
| 236 | 1.2 | Dismantling of 34/ 55 sqmm (2wire) | Elect | Labour | SWR12162 | 2000 | KM | 2400
| 237 | 2 | Supply and Installation of 33KV indoor type Single VCB panel Switchboard (Schneider make ) including the cost of testing and commissioning | Elect | Labour | SWR25187 | 1300000 | EA | 2600000
| 238 | 90 | Fabrication of materials including 2 coats of Red oxide painting Back clamps with 75 x 8 mm MS Flat | Elect | Labour | SWR10319 | 31 | EA | 2790
| 239 | 5 | Fabrication of materials including 2 coats of Red oxide painting Strut clamps with 75 x 8 mm MS Flat | Elect | Labour | SWR11262 | 84 | EA | 420
| 240 | 229.16 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Elect | Labour | SWR10919 | 41 | RMT | 9395.56
| 241 | 7.62 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 26106.12
| 242 | 6 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 6144
| 243 | 6 | Un Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 6144
| 244 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators,transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 16498.5
| 245 | 240 | Laying of XLPE UG cable Six Run including excavation of trench of size 1050mm wide to 1200mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-Along the CC / BT multi layer road requiring compressor-11 KV 3x300 Sqmm Cable | Elect | Labour | SWR12070 | 2173.88 | M | 521731.2
| 246 | 240 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of leadand lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil/CC-11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11973 | 631.06 | M | 151454.4
| 247 | 200 | Laying of XLPE UG Single Run cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs-Along the CC / BT multi layer road requiring compressor-11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11928 | 1073.94 | M | 214788
| 248 | 1440 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 204.1 | M | 293904
| 249 | 160 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x300 Sqmm Cable. | Elect | Labour | SWR11955 | 144.08 | M | 23052.8
| 250 | 20 | Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | Elect | Labour | SWR10391 | 2370.63 | EA | 47412.6
| 251 | 7 | Making of Straight through joints-11 KV 3x300 Sqmm Cable | Elect | Labour | SWR10386 | 3725.45 | EA | 26078.15
| 252 | 50 | Supply of 150 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | Elect | Supply | SMR40078 | 303 | M | 15150
| 253 | 1400 | Supply of 4" B class GI pipe Cost of Pipes and slabs | Elect | Supply | SMR40080 | 740 | M | 1036000
| 254 | 50 | supply of 4" DWC pipe Cost of Pipes and slabs | Elect | Supply | SMR11609 | 759 | M | 37950
| 255 | 440 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours.-11KV | Elect | Labour | SWR21903 | 30 | M | 13200
| 256 | 8 | Loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10238 | 80 | EA | 640
| 257 | 8 | Un Loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10556 | 80 | EA | 640
| 258 | 8 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR10393 | 3200 | EA | 25600
| 259 | 35 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 43197
| 260 | 35 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elect | Labour | SWR10359 | 386 | EA | 13510
| 261 | 8 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 1173.04
| 262 | 35 | Supply of GI eath pipe with 40 mm dia,3mm thcikness with 2.0M Length | Elect | Supply | SMR11480 | 698 | EA | 24430
| 263 | 22 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 58164.26
| 264 | 44 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 3344
| 265 | 44 | Un-Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 2200
| 266 | 22 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 24904
| 267 | 22 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | Elect | Labour | SWR10107 | 700 | EA | 15400
| 268 | 0.682 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 2655.026
| 269 | 28.96 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 190527.84
| 270 | 8.1 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Elect | Labour | SWR10206 | 221 | TO | 1790.1
| 271 | 8.1 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Elect | Labour | SWR10524 | 185 | TO | 1498.5
| 272 | 19.225 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel,iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading )-Above 10 KM and upto 20 KM | Elect | Labour | SWR10132 | 412.08 | TO | 7922.238
| 273 | 10 | Loading of 11 KV AB Cable (XLPE) 3 Core upto 500 Mts. Drum (including Accessories ) | Elect | Labour | SWR12413 | 584 | DR | 5840
| 274 | 10 | Un loading of 11 KV AB Cable (XLPE) 3 Core upto 500 Mts.Drum (including Accessories ) | Elect | Labour | SWR12431 | 438 | DR | 4380
| 275 | 4.9 | Stringing of HT AB Cable with GI Metal Parts-HT AB Cable 11 KV 3x185+70 Sqmm | Elect | Labour | SWR10454 | 41876.1 | KM | 205192.89
| 276 | 69 | Supply of 11KV 3x185+70sq.mm/ 3x70+70sq.mm/3x35+35sq.mm AB cable end Kits | Elect | Supply | SMR11504 | 950 | SET | 65550
| 277 | 2000 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 235000
| 278 | 300 | Drilling of holes upto 20 mm dia using power drills-MS Channel, Angles and flat | Elect | Labour | SWR10307 | 4 | EA | 1200
| 279 | 100 | Cutting charges for MS Sections-MS Channel 100 x 50 mm | Elect | Labour | SWR10294 | 10 | EA | 1000
| 280 | 76 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properlyramming including transport of materials from road side to location excluding pit excavation-11 Mtrs PSCC poles | Elect | Labour | SWR10978 | 4336.85 | EA | 329600.6
| 281 | 76 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)-11 Mtrs long PSCC Poles | Elect | Labour | SWR11180 | 431.97 | EA | 32829.72
| 282 | 76 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | Elect | Labour | SWR10107 | 700 | EA | 53200
| 283 | 100.03 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 658097.37
| 284 | 2 | Loading of Conductor drums | Elect | Labour | SWR10191 | 202 | EA | 404
| 285 | 2 | Un Loading of Conductor drums | Elect | Labour | SWR10509 | 100 | EA | 200
| 286 | 2 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)-Trans 11/12.5/12.9M Spun pole upto 50KM | Elect | Labour | SWR11181 | 858 | EA | 1716
| 287 | 2 | Loading of Spun poles 12.5 M | Elect | Labour | SWR10190 | 548 | EA | 1096
| 288 | 2 | Un Loading of Spun poles 12.5 M | Elect | Labour | SWR10508 | 363 | EA | 726
| 289 | 2 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Spun poles 12.5 Mtrs / 12.9Mtrs PSCC | Elect | Labour | SWR10350 | 4521.66 | EA | 9043.32
| 290 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") | Elect | Labour | SWR11041 | 1466.25 | EA | 2932.5
| 291 | 3.88 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 25526.52
| 292 | 8 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 21960
| 293 | 5000 | Cut-Tree Branch(LT/11/33)&Trnsprt Debris | Elect | Labour | SWR23200 | 4 | EA | 20000
| 294 | 1.65 | Paving out and stringing of conductor by providing temporary stays, tensioning,sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location.-100 Sqmm Single Circuit (3 Conductors) | Elect | Labour | SWR10366 | 13856.7 | KM | 22863.555
| 295 | 12 | Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays | Elect | Labour | SWR10653 | 1435.81 | EA | 17229.72
| 296 | 138 | Loading of 11KV pin insulators/Post type insulators/ Solid core insulators | Elect | Labour | SWR10212 | 1 | CRT | 138
| 297 | 138 | Un Loading of 11KV pin insulators/Post type insulators/ Solid core insulators | Elect | Labour | SWR10530 | 1 | CRT | 138
| 298 | 72 | Loading of 33 & 11 KV Disc insulators | Elect | Labour | SWR12416 | 2 | CRT | 144
| 299 | 72 | Un Loading of 33 & 11 KV Disc insulators | Elect | Labour | SWR10631 | 2 | CRT | 144
| 300 | 2 | Loading of 11 KV Metal parts | Elect | Labour | SWR12402 | 48 | BAG | 96
| 301 | 2 | Un Loading of 11 KV Metal parts | Elect | Labour | SWR12421 | 48 | BAG | 96
| 302 | 46 | Loading of 11 KV V - Cross arms | Elect | Labour | SWR10228 | 4 | EA | 184
| 303 | 46 | Un Loading of 11 KV V - Cross arms | Elect | Labour | SWR10546 | 4 | EA | 184
| 304 | 1 | Transport of steel including line materials such as cross arms, clamps, hardware, cable (loose) and other line materials (Including loading and unloading)-Above 10 KM and upto 20 KM | Elect | Labour | SWR10148 | 481.44 | TO | 481.44
| 305 | 4.752 | Excavation of pits in all soils except hard rock requiring blasting-M-Type Tower (1.2M x 1.2M x 3.3M ) 4.752cum | Elect | Labour | SWR12085 | 1997.93 | EA | 9494.1634
| 306 | 9.504 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-M-Type Tower (1.2M x 1.2M x 3.3M ) 4.752cum | Elect | Labour | SWR12090 | 3592.95 | EA | 34147.3968
| 307 | 2.9 | Dismantling of 11KV 34/55 sqmm SC | Elect | Labour | SWR22065 | 4500 | KM | 13050
| 308 | 2.9 | Restringing of existing loose Lines by removing the pin-binding and jumpers, Providing of temporary stays, providing stiffners pieces, replacement of damaged insulators, alignment of cross arms, pin binding and jumpering after tensioning and removing of the temporary stays complete -Restringing of with 55 Sqmm single ckt 3 cond | Elect | Labour | SWR11308 | 6616 | KM | 19186.4
| 309 | 3 | Supply of M+3 Tower (Galvanized) | Elect | Supply | SMR11683 | 140674.3 | EA | 422022.9
| 310 | 3 | Erection of M+3 Tower (Galvanized) | Elect | Labour | SWR11850 | 64576 | EA | 193728
| 311 | 6 | Supply of material for Extension of 3Mtrs for M+3 (Galvanized) | Elect | Supply | SMR11684 | 28520.64 | EA | 171123.84
| 312 | 6 | Erection of Extension of 3Mtrs for M+3 (Galvanized) | Elect | Labour | SWR11851 | 5168.95 | EA | 31013.7
| 313 | 12 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-9.1 M long PSCC pole | Elect | Labour | SWR10343 | 2400 | EA | 28800
| 314 | 12 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)-9.1 Mtrs long PSCC Poles | Elect | Labour | SWR20308 | 407.29 | EA | 4887.48
| 315 | 88 | Loading of PSCC Poles 9.1 M | Elect | Labour | SWR10188 | 182 | EA | 16016
| 316 | 88 | Un Loading of PSCC Poles 9.1 M | Elect | Labour | SWR10506 | 91 | EA | 8008
| 317 | 12 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | Elect | Labour | SWR10107 | 700 | EA | 8400
| 318 | 23.36 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 153685.44
| 319 | 44 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 22552.2
| 320 | 69 | End Termination of AB cable (each lead):120 Sqmm to 185 Sqmm | Elect | Labour | SWR10667 | 800 | EA | 55200
| 321 | 124 | Straight through joints of AB cable (each lead) Supply and ere Straight line Asmbly kits | Elect | Labour | SWR10672 | 1661 | EA | 205964
| 322 | 34 | Straight through joints of AB cable (each lead) Supply and ere Angle line Asmbly kits | Elect | Labour | SWR10673 | 2124 | EA | 72216
| 323 | 48 | Erection of Assemble Kit for 'T' Branche | Elect | Labour | SWR10671 | 1800 | EA | 86400
| 324 | 48 | Supply and erection of T-Branch kit | Elect | Supply | SWR24971 | 3215 | EA | 154320
| Total | [7 empty] | 18793497.3234
18 % GST | [8 empty] | 3382829.5182
| Electrical Total Incl GST | [7 empty] | 22176326.8416
Civil Portion
1 | 1 | 74 | Level & Clear the Site with the help of JCB including costconveyance of all materials,hire chareges etc complete for finished item of work. | Civil | Labour | SWR34179 | 2165 | Hr | 160210 | 160210
2 | 2 | 4534.75 | Excavation in HDR & hard rock if blasting prohibited in rock in foundation grade levelling including cost of all leads and lifts etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR33018 | 1440 | Cum | 6530040 | 6530040
3 | 3 | 463.5 | Drilling 25mm Dia Holes in Sheet Rock etc., | Civil | Labour | SWR34180 | 144 | M | 66744 | 66744
4 | 4 | 509.5 | Grouting 25mm dia Hole with CementSlurry | Civil | Labour | SWR34460 | 116 | M | 59102 | 59102
5 | 5 | 62.33 | Plain Cement concrete (1:3:6) using 40mm HBG metal , including cost and conveyance of all materials, labour ,all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item of work as directed by engineer-in-charge | Civil | Labour | SWR33029 | 4447 | Cum | 277181.51 | 277181.51
6 | 6 | 157.95 | CRS masonry in CM 1:6 using Hard Granite Stones including cost and conveyance of all materials,labour, seignorage charges, dewatering,scaffolding,curing, all leads and lifts, all incidental charges etc .complete for finished item of work as directed by the Engineer - in - charge. | Civil | Labour | SWR33041 | 4014 | Cum | 634011.3 | 634011.3
7 | 7 | 106.4 | Plain cement concrete 1:2:4 nominal mix using 12 mm HBG metal including cost & conveyance of all materials, labour, seignorage charges , mixing,curing,etc complete for finished item of work as directed by the Engineer-in-charge. | Civil | Labour | SWR33030 | 5562 | Cum | 591796.8 | 591796.8
8 | 8 | 5267.5 | Supplying and filling with borrowed gravel, watering, ramming, consolidating thoroughly complying with the standard specification including cost and conveyance of all materials, labour charges,hire charges of machnery,with all leads and lifts,incidental charges etc complete for finished item work as directed by the Engineer - in - charge. | Civil | Supply | SWR33052 | 252 | Cum | 1327410 | 1327410
9 | 9 | 110.4 | Brick masonary in CM(1:6) including cost and conveyance of all materials, labour charges,curing etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Labour | SWR33068 | 7504 | Cum | 828441.6 | 828441.6
| 10 | 155 | Footings Reinforced cement concerete M20 GRADE Nominal Mix for footings , columns, Beams and Slab using 12mm to 20mm size graded HBG machine crushed metal from approvaed quary giving cube crushing strenth of 20 N /sqm and a minimum of 400 kgs of cement for 1 Cum of concrete including cost and conveyance of all materials,labour, seignorage charges, centering, shuttering, machine mixing,laying concrete, curing, compaction by pin and pan vibrater, supplemented by hand spreeding rodding and tamping, all leads and lifts,all incidental charges etc complete for finished item of work but excuding cost of steel and its fabrication as directed by the Engineer - in - charge . | Civil | Labour | SWR33098 | 8284 | Cum | 1284020 | 1284020
| 11 | 182.3 | Columns Reinforced cement concerete M20 GRADE Nominal Mix for footings , columns, Beams and Slab using 12mm to 20mm size graded HBG machine crushed metal from approvaed quary giving cube crushing strenth of 20 N /sqm and a minimum of 400 kgs of cement for 1 Cum of concrete including cost and conveyance of all materials,labour, seignorage charges, centering, shuttering, machine mixing,laying concrete, curing, compaction by pin and pan vibrater, supplemented by hand spreeding rodding and tamping, all leads and lifts,all incidental charges etc complete for finished item of work but excuding cost of steel and its fabrication as directed by the Engineer - in - charge . | Civil | Labour | SWR33100 | 10979 | Cum | 2001471.7 | 2001471.7
| 12 | 3.6 | Plinth Beams Reinforced cement concerete M20 GRADE Nominal Mix for footings , columns, Beams and Slab using 12mm to 20mm size graded HBG machine crushed metal from approvaed quary giving cube crushing strenth of 20 N /sqm and a minimum of 400 kgs of cement for 1 Cum of concrete including cost and conveyance of all materials,labour, seignorage charges, centering, shuttering, machine mixing,laying concrete, curing, compaction by pin and pan vibrater, supplemented by hand spreeding rodding and tamping, all leads and lifts,all incidental charges etc complete for finished item of work but excuding cost of steel and its fabrication as directed by the Engineer - in - charge . | Civil | Labour | SWR33099 | 10704 | Cum | 38534.4 | 38534.4
| 13 | 0.7 | Lintels Reinforced cement concerete M20 GRADE Nominal Mix for footings , columns, Beams and Slab using 12mm to 20mm size graded HBG machine crushed metal from approvaed quary giving cube crushing strenth of 20 N /sqm and a minimum of 400 kgs of cement for 1 Cum of concrete including cost and conveyance of all materials,labour, seignorage charges, centering, shuttering, machine mixing,laying concrete, curing, compaction by pin and pan vibrater, supplemented by hand spreeding rodding and tamping, all leads and lifts,all incidental charges etc complete for finished item of work but excuding cost of steel and its fabrication as directed by the Engineer - in - charge . | Civil | Labour | SWR33107 | 11139 | Cum | 7797.3 | 7797.3
| 14 | 4.7 | Roof Beams Reinforced cement concerete M20 GRADE Nominal Mix for footings , columns, Beams and Slab using 12mm to 20mm size graded HBG machine crushed metal from approvaed quary giving cube crushing strenth of 20 N /sqm and a minimum of 400 kgs of cement for 1 Cum of concrete including cost and conveyance of all materials,labour, seignorage charges, centering, shuttering, machine mixing,laying concrete, curing, compaction by pin and pan vibrater, supplemented by hand spreeding rodding and tamping, all leads and lifts,all incidental charges etc complete for finished item of work but excuding cost of steel and its fabrication as directed by the Engineer - in - charge . | Civil | Labour | SWR33121 | 10715 | Cum | 50360.5 | 50360.5
| 15 | 14.9 | Roof slab 120 mm thick Reinforced cement concerete M20 GRADE Nominal Mix for footings , columns, Beams and Slab using 12mm to 20mm size graded HBG machine crushed metal from approvaed quary giving cube crushing strenth of 20 N /sqm and a minimum of 400 kgs of cement for 1 Cum of concrete including cost and conveyance of all materials,labour, seignorage charges, centering, shuttering, machine mixing,laying concrete, curing, compaction by pin and pan vibrater, supplemented by hand spreeding rodding and tamping, all leads and lifts,all incidental charges etc complete for finished item of work but excuding cost of steel and its fabrication as directed by the Engineer - in - charge . | Civil | Labour | SWR33128 | 10266 | Cum | 152963.4 | 152963.4
#REF! | 16 | 43 | Providing High Yield Strength Deformed (HYSD)/ Thermo Mechanically Treated (TMT) / Mild steel (MS) steel bars (Fe 415/ Fe 500 grade as per IS 1786-1979) of different diameters for RCC works , including cost and conveyance of all materials, labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings, including all wastages such as overlaps, chairs, spacer bars, and binding wire, all incidental, operational charges and sales and other taxes on all materials etc., complete for finished item of work in all floors.( APSS No.126) as directed by Engineer-in-charge. | Civil | Labour | SWR33144 | 76127 | MT | 3273461 | 3273461
#REF! | 17 | 1309.8 | Providing plastering of 20mm thick to all walls and ceiling of superstructure in two coats with first coat in CM 1:6 of 16mm thick and second coat in Cm 1:4 4mm thick including cost and conveyance of all materials,labour, water charges, curing for specified number of days, cutting grooves, at all heghits, all leads and lifts, incidental and scaffolding, seigniorage charges, etc. complete for finished item of work as directed by the Engineer - in - charge. | Civil | Labour | SWR33163 | 418 | Sqm | 547496.4 | 547496.4
#REF! | 18 | 96.2 | Providing impervious coat over RCC roof slab to requried slopes with 20mm thick in CM 1:3 mixed with approved brand of water proffing compound inclding cost and conveyance of all materials, labour charges, curing, rounding off junctions of wall and slab, all leads and lifts, etc . complete for finished item of work as directed by the Engineer - in - charge. | Civil | Labour | SWR33156 | 447 | Sqm | 43001.4 | 43001.4
#REF! | 19 | 67.8 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work as directed by Engineer-in-charge. | Civil | Labour | SWR33184 | 96 | Sqm | 6508.8 | 6508.8
#REF! | 20 | 7.8 | Supply and fixing of doors with the frames of the door shall be made well seasoned mt wood of cross section 100x75mm. The shutter shall be made isi mark flushed door with laminate both sides with PVC beading 40mm width all round.Frame shall be painted with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary with 3 no 150mm brass hinges 1 no brass door stoper, 1 no 250mm brass aldrops. 2 no 300 mm aluminium tower bolts, 2 no 150mm brass fancy door handlers, 1 no keyless lockset with cp handel. The quoted rate shall include cost and conveyance of the meterials, fixig, labour carges, tools, handles,locking arrangementts and other fixtures & fittings for finished item work as directed by the Engineer - in- charge. | Civil | Supply | SWR33264 | 7314 | Sqm | 57049.2 | 57049.2
#REF! | 21 | 12.6 | Supply and Fixing of Aluminium sliding windows with fixed glass panels using aluminium sections 62x32x1.2mm providing 5mm plain glass fixed to frame with beading gasket and glazing clips with all accessories,locking arrangements including cost and conveyance of all materials,labour charges etc. complete for finished item of work and as directed by the Engineer-in-charge.. | Civil | Supply | SWR33277 | 3623 | Sqm | 45649.8 | 45649.8
#REF! | 22 | 14.4 | Supplying and fixing of MS safety grill with peripheral frame of ISA 25x25x4mm and horizontal & vertical 8mm square rods and including cost and coveyance of all mateirals with all leads and lifts, labour charges, painting charges complete for finished item of work as directed by Engieer-in-chargea. | Civil | Supply | SWR33310 | 2990 | Sqm | 43056 | 43056
#REF! | 23 | 96 | Flooring with double machine polished and hand cut Shabad stone 20mm thick of approved colour, quality and size over a bed of cement mortar 1:3 20mm thick including cost of all materials, labour,with all leads and lifts, jointing and pointing with cement, etc, complete for finished item of work as directed by Engineer-in-charge | Civil | Labour | SWR33219 | 663 | Sqm | 63648 | 63648
#REF! | 24 | 7.7 | Providing skirting with polished shabad stone including cost & conveyance of all materials,labour charges etc complete for finished item of work as directed by Engineer-in-charge. | Civil | Labour | SWR33236 | 723 | Sqm | 5567.1 | 5567.1
#REF! | 25 | 999.6 | Painting with two coats of ACE paint over a coat of primer including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the Engineer-in-charge. | Civil | Labour | SWR33356 | 210 | Sqm | 209916 | 209916
#REF! | 26 | 237 | Painting with two coats of OBD over a coat of primer including cost and conveyance of all materials ,labour charges etc. complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33333 | 146 | Sqm | 34602 | 34602
22 | 27 | 192 | Supply and fixing of fencing of welded wire mesh with support channels of 75x 40mm and angles around of 25x25x3mm including cost and conveyance of all materials ,fabrication charges,painting charges etc. complete for finished item of work as directed by the Engineer-in-charge. | Civil | Supply | SWR33403 | 2310 | Sqm | 443520 | 443520
23 | 28 | 13.1 | Providing RCM Drop Walls in CM 1:2 of 40mm thick over rabbit wire mesh including cost and conveyance of all meterials, labour charges, curing ,at all levels, leads and lifts, seignioage charges etc., complete, but excluding cost of steel as per the approved drawing for finished item of work as directed by the Engineer -in -charges | Civil | Labour | SWR33203 | 2549 | Sqm | 33391.9 | 33391.9
24 | 29 | 100 | Supply and fixing 25mm dia 1.5mm thick ( concealed) PVC pipe alog with reinforcement to be laid in slab including No. 14 SWG GI wire for earth contunity, cost of pipe, binding wire and all labour charges etc complete for finished item of work. | Civil | Supply | SWR33438 | 97 | Rmt | 9700 | 9700
25 | 30 | 70 | Supply and fixing 32mm dia 2mm thick ( concealed) PVC pipe in the wall including No 14 SWG GI wire for earth contunity, cost of pipe, binding wire and all labour charges etc complete for finished item of work. | Civil | Labour | SWR33439 | 125 | Rmt | 8750 | 8750
26 | 31 | 50 | Wiring with 2X1.0 Sqm(14/0.3mm) PVC insulated flexiable copper cable in the existing metalic/Non metalic conduit pipe with 6A mini modular SP switch, mounted on metalic box covereds with appropriate front plate modules etc ceiling rose including cot and conveyance of all mateials, labour charges complete for light points, bell points and fan points in non residential builsing except circuit moving finished in all types masonary as directed by department. | Civil | Labour | SWR33598 | 728 | M | 36400 | 36400
27 | 32 | 8 | Supply and fixing of 6A 3/2 pin flush type plug socket with 6A flush type marked switch control on a common board with earth continuity including wire leads earth connections along with all labour charges etc. complete | Civil | Supply | SWR33462 | 314 | No | 2512 | 2512
28 | 33 | 8 | Supply and fixing of 16A 3pin flush type plug socket and 16A flush type fuse unit and 16A switch control. | Civil | Supply | SWR33463 | 395 | No | 3160 | 3160
29 | 34 | 12 | Supply and fixing of slanting holders with 100W bulb with all connections and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | Supply | SWR33484 | 141 | No | 1692 | 1692
30 | 35 | 8 | Supply and fixing of patty type tube light fitting with 4' 0" - 40W tube light,40W copper choke,starter,labour charges etc. complete for finished item of work as directed by the engineer-in-charge. | Civil | Supply | SWR33545 | 919 | No | 7352 | 7352
31 | 36 | 150 | Supply and run of 2 of 14/.3mm (1.00 Sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Civil | Supply | SWR33494 | 56 | Rmt | 8400 | 8400
32 | 37 | 139 | Supply and run of 2 of 36/0.3 (2.5sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Civil | Supply | SWR33497 | 103 | Rmt | 14317 | 14317
33 | 38 | 1 | Supply & fixing TPN Distribution board with IP-42 protection (Metal Door)suitable for single phase ELCB/RCCB/FP Isolator as incomer and 10kA SP 6 No.s MCBs as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Supply | SWR33526 | 11353 | No | 11353 | 11353
34 | 39 | 1 | Providing independent earthing for main switches,IC cutouts and motors using 40mm. Dia. B-class G.I.Pipe of 2.5' length duly providing 12mm. Dia. 6No. Holes and required bolts,nuts and washers,including filling with equal preparation of salt and charcoal in layers and labour charges etc. complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33596 | 5345 | No | 5345 | 5345
35 | 40 | 4 | Supply and Fixing of 48" ceiling fan of bajaj make(or equivalent make) including cost material,labour charges etc. complete for finished item of work as directed by the engineer-in-charge. | Civil | Supply | SWR33563 | 2277 | No | 9108 | 9108
36 | 41 | 17 | Supply and fixing of ceramic tiles fantacy for dadoing including cost and conveyance of all materials,labour charges etc. complete for finished item of work as directed by the engineer-in-charge. | Civil | Supply | SWR33224 | 763 | Sqm | 12971 | 12971
37 | 42 | 1 | Supply and fixing of European Water Closet of first quality conforming IS2556-part-21973 of Parry, Neycer or Hindhusthan, make with 'P' or 'S' trap etc,white glazed complete for finished item of work as directed by the engineer-in-charge. | Civil | Supply | SWR34314 | 2228 | No | 2228 | 2228
38 | 43 | 1 | PVC low level system parry ware , slim line with internal components & short ben 10 liters capacity dual flush including cost and conveyance of all materials and labour charges for finished item of work | Civil | Labour | SWR34376 | 2032 | No | 2032 | 2032
39 | 44 | 2 | Supply and Fixing 4" PVC floor trap including labour charges etc. complete for finished item of work as directed by the engineer-in-charge. | Civil | Supply | SWR34386 | 269 | No | 538 | 538
40 | 45 | 2 | Supply,fixing 4" dia. PVC Plain Bend including cost etc. complete for finished item of work as directed by the engineer-in-charge. | Civil | Supply | SWR34382 | 84 | No | 168 | 168
41 | 46 | 2 | Supply,fixing 4" dia. PVC Door Bend including cost etc. complete for finished item of work as directed by the engineer-in-charge. | Civil | Supply | SWR34383 | 113 | No | 226 | 226
42 | 47 | 1 | S&Fixing 150mm x 100mm SWG gully traps Ist class grating & constg brick masonry in CM (1:6) prop inter mediate chamber fitted with CI frame etc complete. | Civil | Supply | SWR34286 | 767 | No | 767 | 767
43 | 48 | 15 | Supply and Fixing 4" dia 3M Single socket PVC pipe including labour charges etc. complete for finished item of work as directed by the engineer-in-charge. | Civil | Supply | SWR34377 | 462 | Rmt | 6930 | 6930
44 | 49 | 20 | Supply,laying and jointing 152.4 mm SWG pipe including excavation of trenches etc. complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34284 | 893 | Rmt | 17860 | 17860
45 | 50 | 5 | Constructing (457.2mmx457.2mm) Brick in CM(1:6) prop Masonry inspection chamber and fitted with light weight CI frame and cover etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34296 | 8766 | No | 43830 | 43830
| 51 | 30 | 15.90mm OD Pipe - SDR 11 Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007) | Civil | Supply | SWR34361 | 239 | Rmt | 7170 | 7170
| 52 | 125 | 22.20mm OD Pipe - SDR 11 Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007) | Civil | Supply | SWR34362 | 313 | Rmt | 39125 | 39125
| 53 | 100 | 28.60mm OD Pipe - SDR 11 Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007) | Civil | Supply | SWR34363 | 410 | Rmt | 41000 | 41000
#REF! | 54 | 1 | Supply and fixing of 15mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Civil | Supply | SWR34344 | 230 | No. | 230 | 230
#REF! | 55 | 1 | Supply and fixing of 20mm dia. GM Ball valve including labour charges complete for finished item of work as directed by the engineer-in-charge. | Civil | Supply | SWR34345 | 331 | No | 331 | 331
#REF! | 56 | 2 | Supply and fixing of 25mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Civil | Supply | SWR34346 | 466 | No | 932 | 932
#REF! | 57 | 1 | Supply and fixing of 12.7mm dia. concealed stop cock including labour charges complete for finished item of work as directed by the engineer-in-charge. | Civil | Supply | SWR34328 | 721 | No | 721 | 721
#REF! | 58 | 35 | Supply and fixing of 12.7mm bib tap Indian make including labour charges complete for finished item of work as directed by the engineer-in-charge. | Civil | Supply | SWR34329 | 298 | No | 10430 | 10430
#REF! | 59 | 1000 | Providing and placing on Terrace polyetheylene water storage tank with double layer approved brand and manufacture with cover complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34375 | 10 | Ltr | 10000 | 10000
#REF! | 60 | 11.86 | Supply and fixing of ms gates of approved design including cost and conveyance of all materials,fabrication charges etc complete for finished item of work. | Civil | Supply | SWR33404 | 5299 | Sqm | 62846.14 | 62846.14
#REF! | 61 | 1 | Geophysical Investgation charges for water point by Geologist | Civil | Labour | SWR33608 | 5000 | EA | 5000 | 5000
55 | 62 | 475 | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete | Civil | Labour | SWR33609 | 336 | RMT | 159600 | 159600
56 | 63 | 40 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Supply | SWR33611 | 883 | RMT | 35320 | 35320
57 | 64 | 1 | Supply and erecting, ISI mark submersible 5.0 HP, Three Phase SubMrsbl Pumpset 5HP 12-16Stages suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Supply | SWR33640 | 48007 | EA | 48007 | 48007
58 | 65 | 350 | Supply and fixing of HDPE pipe 40mm dia of 6Kg/cm2 including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Supply | SWR34410 | 180 | RMT | 63000 | 63000
59 | 66 | 1 | Supply and erecting D.O.L Starter 415V , 3 phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Supply | SWR33645 | 7854 | EA | 7854 | 7854
60 | 67 | 450 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Supply | SWR33641 | 192 | RMT | 86400 | 86400
61 | 68 | 3 | S&F of poly vinyl acrylic board of approved quality including cost of all materials and labour charges complete for finished item. | Civil | Supply | SWR33422 | 3553 | Sqm | 10659 | 10659
62 | 69 | 1 | Providing supply of electricity to the site premises through customer service centre duly applying for new connection including service wire, application fee and other missalaneous charges prescribed by APCPDCL complete for the finished item of work. | Civil | Labour | SWR33425 | 5408 | Job | 5408 | 5408
63 | 70 | 4534.75 | Carting away dismantled material | Civil | Labour | SWR34151 | 270 | Cum | 1224382.5 | 1224382.5
64 | 71 | 4 | Providing contour surveying maps with total station including preparation of boundary and contour levels with 2 No.s hard copies and soft copies complete for finished items of work. | Civil | Labour | SWR33427 | 5665 | EA | 22660 | 22660
65 | 72 | 5580 | Design and submisiion of 2 sets of structural design drawings with soft copy complete finished item of work | Civil | Labour | SWR33426 | 5 | FT2 | 27900 | 27900
66 | 73 | 2 | Providing report on Soil Bearing Capacity by Geologist/Geo-technical investigators with the sample collected from construction site complete for finished item of work | Civil | Labour | SWR34097 | 4500 | EA | 9000 | 9000
67 | 74 | 343.47 | Seigniorage Charges - Sand | Civil | Supply | SWR34470 | 40 | Cum | 13738.8 | 13738.8
68 | 75 | 649.35 | Seigniorage Charges - Metal | Civil | Supply | SWR34471 | 97.5 | Cum | 63311.625 | 63311.625
69 | 76 | 5267.5 | Seigniorage Charges - Gravel | Civil | Supply | SWR34472 | 30 | Cum | 158025 | 158025
70 | 77 | 1 | Provd-DGPS & Total Staion Survey | Civil | Labour | SWR34506 | 5000 | EA | 5000 | 5000
|  |  | Total | [5 empty] | 21140642.175 | 21140642.175
|  |  | 18% GST | [5 empty] | 3805315.5915
|  |  | Civil Total incl GST | [5 empty] | 24945957.7665
| Total Cost (Without GST)=Electrical + Civil | [7 empty] | 39934139.4984
| Total Cost (With 18 % GST)=Electrical + Civil | [7 empty] | 47122284.6081
39934139.51
7188145.1118
47122284.6218

## estimate
Activity wise