## Sheet1
"Shifting of 33kV & 11kV line due to road widening works at Government School to Q-mart kondapur of M/s Deputy Commissioner GHMC circle No.20, Sherlingampally zone, Hyderabad in Cyber city Operation circle in sub-division 1 of WCGH division of Master plan Ranga Reddy circle under DC works (CC915233553299)"
WBS No. G-2023-13-04-01-01-001
Sl.No | Estimate Quantity(Only Figures) | PARTICULARS | Work Type | Item Short Description | SWR No/APSS/Morth cl.No | Rate (INR) (Upto 2 Decimals) | UOM | Amount
1 | 7 | Making of Straight through joint 33kv 3x400 xlpe | Elecy | Labour | SWR10382 | 5700.78 | EA | 39905.46
2 | 12 | Making of Outdoor/Indoor End Termination 33kv 3x400 xlpe | Elecy | Labour | SWR10387 | 2764.76 | EA | 33177.12
3 | 425 | Lay-DR 33KV 3x400sqmm UG Cb HG/BC/CC/BT Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC 33 KV 3x400 Sqmm Cable. | Elecy | Labour | SWR11972 | 749 | M | 318325
4 | 30 | Lay-SR 33KV 3x400sqmm UG Cb HG/BC/CC/BT Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road 33 KV 3x400 Sqmm Cable. | Elecy | Labour | SWR11918 | 572.1 | M | 17163
5 | 425 | Laying of 2nd cable in excavated trench | Elecy | Labour | SWR10988 | 204.1 | M | 86742.5
6 | 10 | Raise-SR 33KV 3x400sqmm UG Cb on support Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) 33 KV 3x400 Sqmm Cable. | Elecy | Labour | SWR11954 | 135.66 | M | 1356.6
7 | 70 | Raise-DR 33KV 3x400sqmm UG Cb on support Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe). 33 KV 3x400 Sqmm Cable. | Elecy | Labour | SWR12004 | 323.85 | M | 22669.5
8 | 3 | LOADING of 33 KV AB SWCH Con 400/800 A | Elecy | Labour | SWR10239 | 126 | EA | 378
9 | 3 | UNLOADING of 33 KV AB SWCH Con 400/800 A | Elecy | Labour | SWR10557 | 79 | EA | 237
10 | 3 | Erection of 33 KV AB Switch including alignment and earthing | Elecy | Labour | SWR10392 | 4500 | EA | 13500
11 | 16 | LOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10204 | 76 | EA | 1216
12 | 16 | UNLOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10522 | 50 | EA | 800
13 | 1.35 | LOADING of MS Channel,Angles,Flats&Rods | Elecy | Labour | SWR10206 | 221 | TO | 298.35
14 | 1.35 | UNLOADING of MS Channel,Angles,Flats&Rod | Elecy | Labour | SWR10524 | 185 | TO | 249.75
15 | 5.35 | TRANSPORT OF STEEL 10 TO 20KM Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM. | Elecy | Labour | SWR10132 | 412.08 | TO | 2204.628
16 | 10 | EXCAV. OF PIT 0.75 M x 0.9 M x 1.95 M Excavation of pits in all soils except hard rock requiring blasting 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M (1.31 cum). | Elecy | Labour | SWR10108 | 629.85 | EA | 6298.5
17 | 10 | Fabrication of 175x85/150x75mm RS joist Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elecy | Labour | SWR10642 | 512.55 | EA | 5125.5
18 | 3 | Erect-33KV DP Structure with RS Joist Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting. 33 KV DP Structure with 175x85/150x75mm RS joist. | Elecy | Labour | SWR11276 | 5670 | SET | 17010
19 | 5.35 | Sup Material for 1st coat Al. Painting. Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elecy | Supply | SMR40009 | 2181 | TO | 11668.35
20 | 5.35 | Sup Material for 2nd coat Al. Painting. Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elecy | Supply | SMR40010 | 1293 | TO | 6917.55
21 | 5.35 | Labour for 1st coat Al. Painting. Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elecy | Labour | SWR10877 | 851 | TO | 4552.85
22 | 5.35 | Labour for 2nd coat Al. Painting. Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elecy | Labour | SWR10879 | 482 | TO | 2578.7
23 | 4 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elecy | Labour | SWR11230 | 1024 | DR | 4096
24 | 4 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elecy | Labour | SWR11231 | 1024 | DR | 4096
25 | 2 | Transport of Cond Drum,VCBs >30 & <50Km Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Above 30 Km and upto 50 Km with Lorry for each trip Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates | Elecy | Labour | SWR11863 | 4372.74 | EA | 8745.48
26 | 6 | LOADING of 33 KV10 KA Las Station type | Elecy | Labour | SWR10266 | 41 | EA | 246
27 | 6 | UNLOADING of 33 KV10 KA LAs Station type | Elecy | Labour | SWR10584 | 35 | EA | 210
28 | 2 | Erection of 33 KV LAS station/Line type including earthing | Elecy | Labour | SWR10396 | 880 | SET | 1760
29 | 100 | Supply of GI Bolts & Nuts,Washers etc., | Elecy | Supply | SMR11488 | 117.5 | KG | 11750
30 | 10.5 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement. | Elecy | Labour | SWR10356 | 6579 | M3 | 69079.5
31 | 1 | Submission of auto CAD Drawing as per pole schedule (Detailed survey and sketch) upto 10KM | Elecy | Labour | SWR12104 | 6000 | LS | 6000
32 | 6 | Supply & Erection of Smart RFID marker | Elecy | Labour | SWR25089 | 2745 | EA | 16470
33 | 78 | Supply of 6" B Class GI pipe 5mm thck 20Kg/M | Elecy | Supply | SMR40081 | 1044 | M | 81432
34 | 80 | Supply of 250 mm Hume pipe of class NP3 Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | Elecy | Supply | SMR40077 | 363 | M | 29040
35 | 425 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elecy | Labour | SWR21903 | 30 | M | 12750
36 | 3 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elecy | Labour | SWR12331 | 146.63 | EA | 439.89
37 | 3 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elecy | Labour | SWR10881 | 142 | EA | 426
38 | 11 | Dismantle-Spun poles 11 Mtrs PSCC Dismantling of Damaged Poles, not required and available in the middle of roads, transporting to stock point etc. | Elecy | Labour | SWR11327 | 2154.75 | EA | 23702.25
39 | 0.52 | Dismantling of 100 Sqmm conductor SC Dismantling of 100 Sqmm AAA/ACSR Conductor | Elecy | Labour | SWR22063 | 8274.75 | KM | 4302.87
40 | 5 | Dismantle-Box pole 9/10/11 Mtr Dismantling of Damaged Poles, not required and available in the middle of roads, transporting to stock point etc. | Elecy | Labour | SWR11329 | 1130 | EA | 5650
41 | 3 | Dismantle of 33KV Line AB Switch | Elecy | Labour | SWR12176 | 1281.38 | EA | 3844.14
42 | 1.575 | LOADING of MS Scrap | Elecy | Labour | SWR10258 | 578 | TO | 910.35
43 | 1.575 | UNLOADING of MS Scrap | Elecy | Labour | SWR10576 | 578 | TO | 910.35
44 | 0.206 | LOADING of ACSR conductor scrap | Elecy | Labour | SWR10257 | 491.02 | TO | 101.1501
45 | 0.206 | UNLOADING of ACSR conductor scrap | Elecy | Labour | SWR10575 | 491.02 | TO | 101.1501
46 | 1 | Erection of 9/10/11Meter Box pole Erection of Box pole 9/10/11 Mtr in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Elecy | Labour | SWR11266 | 2643.83 | EA | 2643.83
47 | 0.03 | Stringing 100sqmm 33/11kv Line 3 Cond SC Paving out and stringing of 100 Sqmm Single Circuit (3 Conductors) conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location | Elecy | Labour | SWR10366 | 13856.67 | KM | 415.7001
48 | 9 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elecy | Supply | SMR11482 | 3486 | EA | 31374
49 | 9 | ERECT. OF LINES-Providing of earthing Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elecy | Labour | SWR10357 | 1234.2 | EA | 11107.8
50 | 9 | ERECT. OF LINES-Providing of RCC collar Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elecy | Labour | SWR10359 | 386 | EA | 3474
51 | 0.2 | Stringing of AB cbl 11 KV 3x185+70 Sqmm Stringing of HT 11 KV 3x185+70 Sqmm AB Cable with GI Metal Parts | Elecy | Labour | SWR10454 | 41876.1 | KM | 8375.22
52 | 14 | Erection of 9/10/11Meter Box pole Erection of Box pole 9/10/11 Mtr in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Elecy | Labour | SWR11266 | 2643.83 | EA | 37013.62
53 | 14 | Fabrication of 175x85/150x75mm RS joist Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elecy | Labour | SWR10642 | 512.55 | EA | 7175.7
54 | 14 | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') Excavation of pits in all soils except hard rock requiring blasting 8.0Mtrs PSCC Poles - 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum. | Elecy | Labour | SWR10105 | 650 | EA | 9100
55 | 14.7 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement. | Elecy | Labour | SWR10356 | 6579 | M3 | 96711.3
56 | 50 | Supply of GI Bolts & Nuts,Washers etc., | Elecy | Supply | SMR11488 | 117.5 | KG | 5875
57 | 14 | Painting of Name Plates for any equipmen | Elecy | Labour | SWR10963 | 122 | EA | 1708
58 | 15 | Supply and ere Straight line Asmbly kits | Elecy | Labour | SWR10672 | 1661 | EA | 24915
59 | 5 | Supply and ere Angle line Asmbly kits | Elecy | Labour | SWR10673 | 2124 | EA | 10620
60 | 15 | Supply of Suspension Clamp Assembly & Eye Hook-M | Elecy | Supply | SMR11492 | 65 | EA | 975
61 | 27 | Supply of 11KV AB cable end kits | Elecy | Supply | SMR11504 | 950 | SET | 25650
62 | 27 | End Termnation of AB cable 120 to 185 Sqmm | Elecy | Labour | SWR10667 | 800 | EA | 21600
63 | 5 | Supply and erection of T-Branch kit | Elecy | Labour | SWR24971 | 3215 | EA | 16075
64 | 6 | Supply of GI pipe 40 mm dia, 2 mtrs, 3mm thickness with bolts and nuts | Elecy | Supply | SMR40091 | 733 | EA | 4398
65 | 6 | Earthing of 11KV 3x185+1x75 AB Cb-GIStrip&Pipe | Elecy | Labour | SWR20612 | 500 | EA | 3000
66 | 60 | S&R 25x6mm GI Strip for Earthing | Elecy | Labour | SWR34252 | 113 | M | 6780
67 | 6 | ERECT. OF LINES-Providing of RCC collar Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elecy | Labour | SWR10359 | 386 | EA | 2316
68 | 0.22 | Stringing 100sqmm 33/11kv Line 3 Cond SC Paving out and stringing of 100 Sqmm Single Circuit (3 Conductors) conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location | Elecy | Labour | SWR10366 | 13856.68 | KM | 3048.4696
69 | 4 | Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays | Elecy | Labour | SWR10653 | 1435.81 | EA | 5743.24
70 | 7.2 | Sup Material for 1st coat Al. Painting. Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elecy | Supply | SMR40009 | 2181 | TO | 15703.2
71 | 7.2 | Sup Material for 2nd coat Al. Painting. Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elecy | Supply | SMR40010 | 1293 | TO | 9309.6
72 | 7.2 | Labour for 1st coat Al. Painting. Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elecy | Labour | SWR10877 | 851 | TO | 6127.2
73 | 7.2 | Labour for 2nd coat Al. Painting. Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elecy | Labour | SWR10879 | 482 | TO | 3470.4
74 | 0.25 | Dismantling of 11kV 34/ 55 Sqmm SC | Elecy | Labour | SWR22065 | 4500 | KM | 1125
75 | 0.17 | Dismantle of 11KV AB Cb 3x185+70Sqmm | Elecy | Labour | SWR12161 | 18972 | KM | 3225.24
76 | 4 | Dismantle of 9.1 M long PSCC pole Dismantling of Damaged Poles, not required and available in the middle of roads, transporting to stock point etc. | Elecy | Labour | SWR11320 | 948.09 | EA | 3792.36
77 | 2 | Dismantle of Box pole 9/10/11 Mtr Dismantling of Damaged Poles, not required and available in the middle of roads, transporting to stock point etc. | Elecy | Labour | SWR11329 | 1130 | EA | 2260
78 | 1 | Transport of Cond Drum,VCBs >10 & <20Km Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Above 10 Km and upto 20 Km with Lorry for each trip. Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates | Elecy | Labour | SWR11861 | 3299.7 | EA | 3299.7
79 | 1 | LOADING of Conductor drums | Elecy | Labour | SWR10191 | 202 | EA | 202
80 | 1 | UNLOADING of Conductor drums | Elecy | Labour | SWR10509 | 100 | EA | 100
81 | 28 | LOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10204 | 76 | EA | 2128
82 | 28 | UNLOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10522 | 50 | EA | 1400
83 | 7.25 | TRANSPORT OF STEEL MATERIAL 10 TO 20KM Transport of steel including line materials such as cross arms, clamps, hardware, cable (loose) and other line materials (Including loading and unloading) Above 10 KM and upto 20 KM. | Elecy | Labour | SWR10148 | 481.44 | TO | 3490.44
84 | 1 | LOADING of 11 KV AB Cable (XLPE) 3 Core Loading of 11 KV AB Cable (XLPE) 3 Core upto 500 Mts. Drum (including Accessories ) | Elecy | Labour | SWR12413 | 584 | DR | 584
85 | 1 | UNLOADING of 11 KV AB Cable (XLPE) 3 Cor Un loading of 11 KV AB Cable (XLPE) 3 Core upto 500 Mts. Drum (including Accessories ) | Elecy | Labour | SWR12431 | 438 | DR | 438
86 | 1 | Transport of Cond Drum,VCBs >10 & <20Km Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Above 10 Km and upto 20 Km with Lorry for each trip Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates | Elecy | Labour | SWR11861 | 3299.7 | EA | 3299.7
87 | 0.615 | LOADING of MS Scrap | Elecy | Labour | SWR10258 | 578 | TO | 355.47
88 | 0.615 | UNLOADING of MS Scrap | Elecy | Labour | SWR10576 | 578 | TO | 355.47
89 | 2 | Supply of M+3 Tower (Galvanized) | Elecy | Supply | SMR11683 | 140674.3 | EA | 281348.6
90 | 2 | Supply of material for Extension of 3Mtrs for M+3 (Galvanized) | Elecy | Supply | SMR11684 | 28520.64 | EA | 57041.28
91 | 2 | Erection of M+3 Tower (Galvanized) | Elecy | Labour | SWR11850 | 64576 | EA | 129152
92 | 2 | Erection of Extension of 3Mtrs for M+3 (Galvanized) | Elecy | Labour | SWR11851 | 5168.95 | EA | 10337.9
93 | 9.502 | Earth work excav hard rock bould <3cum Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) (other than SS) Earth work excavtion hard rock boulders. | Elecy | Labour | SWR10856 | 1318.35 | M3 | 12526.9617
94 | 1 | Erection of 11kv ABSwitch incl earthing Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elecy | Labour | SWR10393 | 3200 | EA | 3200
95 | 1 | Dismantle of 11KV Line AB Switch | Elecy | Labour | SWR12177 | 1000.88 | EA | 1000.88
96 | 1 | Loading of 11KV AB Switch Conventional type | Elecy | Labour | SWR10238 | 80 | EA | 80
97 | 1 | Un loading of 11KV AB Switch Conventional type | Elecy | Labour | SWR10556 | 80 | EA | 80 | 927452.82
Schedule Amount Total | [7 empty] | 1773965.7696 | 846512.95
1773965.77
|  | Total Schedule Amount | 1773965.7696