##### TENDER SPECIFICATION

## STN-746/21

## FOR

##### THREE PHASE, ELECTRONIC METER WITH NET-METERING

##### (10-40A) FEATURES IN PP BOX (CLASS 1.0 ACCURACY)

TABLE OF CONTENTS

SECTION	DESCRIPTION			    		PAGE NO.

I   		Notice inviting bids					        	4-6

II		Salient Features of the Bid				        	7

III		General Terms and Conditions Of Contract		        	8-33

IV		Schedule of Requirements					34

V		Qualification Requirements					35-36

VI		Technical 					                    	37-84

VII		  Sample Forms

1)	Bid Form			                    			85

2a) 	Bid Security Form						86

2b)	Performance Security Form				      	87

3)	Contract Form							88-89

4)	Performance Statement                                                       		90

5)	Details to be furnished by the Manufacturer (FORMAT-A) 	91

6)      	Schedule of deviations (Technical & Commercial)             	 	82-93

7)	Declaration Form						 94

NOTE:

1.	Payment terms, Delivery period, Performance Bank Guarantee, Taxes and Duties” should be in line with the terms and conditions of the specification. If any bidder does not meet any one of the conditions, such tender will not be considered. Please note that the conditional offers are also not considered. Hence the bidder shall submit the tender in line with the terms and conditions of the specification.

2.	The bidders shall check the website www.tssouthernpower.com and www.tender.telangana.gov.in for amendments, if any, upto one day prior to the date of tender opening. The amendments shall be binding on the bidders.

3.	The purchaser will not be responsible for any damage that may be caused to the samples at any time.

4.	The bidder shall furnish required Bid Security amount and validity as per specification.  If the bidder fails to furnish bid security amount and bid validity as stipulated in the specification, such tender bid will not be considered for further evaluation.

5.	The prospective bidders shall attend the pre-bid meeting (date and time in NIT) for any queries.  The discussed queries shall be submitted in the form of a letter during pre bid meeting or within 24 hrs of pre bid meeting.  Any new queries received after pre bid meeting are not liable to be considered.

6.	The bid evaluation will be carried out based on the documents uploaded through www.tender.telangana.gov.in against this tender.

7. 	The Bids received with any details pertaining to prices in the offline mode will be liable for rejection.

8.	In e-procurement commercial stage, if F&I charges are applicable then mention whether F&I charges entered are exclusive/inclusive of GST in the remarks section. If not mentioned in remarks, F&I charges will be considered as inclusive of GST.

9.	EMD Exemption is considered only for Government Firms.

Ph : 040 – 23431033, 23431448

Fax : 040 - 23431034

CHIEF GENERAL MANAGER (P&MM)

TSSPDCL

| Energy Saved is |  | SOUTHERN POWER DISTRIBUTION COMPANY OF TELANGANA LTD. 4th Floor, Corporate Office, Mint Compound, Hyderabad |
| --- | --- | --- |

# e-Procurement Tender Notice (Paper Notification)

TSSPDCL intends to float tenders for procurement of (a) Supply, Erection and Commissioning OF 11KV 2 MVAR/ 1 MVAR Capacitor Banks with associated equipment (b) LTCT meters with 100/5A (with IRDA Port) of class 0.5S accuracy with  4 CTs in PP Box with Net-metering features (c) 3-Ph (10-40)A Meter with PP Box (Net meters) on                    e-procurement platform and (d) 11KV 200A (TT) AB Switches with porcelain typesolid coreInsulators

For further details of each item above, please visitwww.tssouthernpower.com, www.tender.telangana.gov.in and www.auction.telangana.gov.in.

Phone: 040-23431319, 1035, 1026, 1448

Sd/-

(U. BALA SWAMY)

CHIEF GENERAL MANAGER (P&MM)

ONLINE VERSION

Tender Notice No : STN-746/21

| Notice Inviting Tender Details |  |  |
| --- | --- | --- |
| S.No | Description |  |
| 1 | Department Name | TSSPDCL |
| 2 | Office | Purchases & Material Management Wing, Corporate Office, TSSPDCL |
| 3 | Tender Number | STN-746/21 |
| 4 | Tender Subject | Three phase, Electronic meter with net-metering (10-40A) features in PP Box (class 1.0 accuracy) |
| 5 | Delivery Schedule | The supplies shall commence in 45 days and complete within 3 months from the date of receipt of purchase order (For trial orders it is in proportion to the quantity quoted) |
| 6 | Tender Type | Open |
| 7 | Tender Category | NA |
| 8 | Bid Security (INR) | (i) 2% of the Ex-works quoted value (plus with GST @18%) (or) (ii) Exemption letter of Bid Security in case of Govt. firms. |
| 9 | Bid Security Payable to | In the form of DD in favour of Pay Officer/TSSPDCL / Hyd or BG from Nationalized/Scheduled Bank as per format 2(a). The validity of the bank guarantee shall be upto bid validity +45 days from the date of tender opening. |
| 10 | Processing Fee (INR) | NIL |
| 11 | Transaction Fee | Transaction fee: All the participating bidders who submit the bids have to pay an amount @ 0.03% of their final bid value online with a cap of Rs.10,000/- for quoted value of purchase upto Rs.50 crores and Rs.25000/- if the purchase value is above Rs.50 crores & service tax applicable as per GST as levied by Govt. of India on transaction fee through online in favour of M/s. TSTS. The amount payable to M/s. TSTS is non refundable. Corpus Fund: Successful bidder has to pay an amount of 0.04% on quoted value through demand draft in favour of Managing Director, TSTS, Hyderabad towards corpus fund at the time of concluding agreement. |
| 12 | Transaction Fee Payable to | TSTS, Hyderabad |
| 13 | Date & time of pre-bid meeting with manufacturer | 24-07-2021 at 11:30Hrs |
| 14 | Schedule Sale opening date | 15-07-2021 from 14:00Hrs |
| 15 | Schedule Sale closing Date | 03-08-2021 Upto 17:00 Hrs. |
| 16 | Bid Submission Closing Date & time | 04-08-2021 Upto 12:00 Hrs |
| 17 | Bid submission | On Line |
| 18 | Pre-Qualification& Technical Bid Opening Date (Qualification and Eligibility Stage and Technical Bid Stage) | 04-08-2021 at 15:00 Hrs. |
| 19 | Price Bid Opening Date (Financial Bid Stage) | 07-08-2021 at 12:00 Hrs |
| 20 | Place of Tender Opening | O/o Chief General Manager/P&MM TSSPDCL, 4th Floor, Corporate Office, Mint Compound, Hyderabad – 500 004. |
| 21 | Officer Inviting Bids/ Contact Person | Chief General Manager/P&MM/TSSPDCL/HYDERABAD |
| 22 | Address/E-mail id | O/o. Chief General Manager/P&MM TSSPDCL, 4th Floor, Corporate Office, Mint Compound, Hyderabad – 500 004 |
| 23 | Contact Details/Telephone, Fax | Ph. No. 040-23431448, 040-23431319. Fax No. 040-23431034 |
| 24 | Eligibility Criteria | As per Section VI |
| 25 | Procedure for Bid Submission | Bids shall be submitted online on www.eprocurement.gov.in platform - The participating bidders in the tender should register themselves free of cost on e-procurement platform in the website www.eprocurement.gov.in. - Bidders can log-in to e-procurement platform in Secure mode only by signing with the Digital certificates. - The bidders who are desirous of participating in e-procurement shall submit their technical bids, price bids as per the standard formats available at the e-market place. - The bidders should scan and upload the following documents in support of technical bids. The bidders shall sign on all the statements, documents certificates uploaded by him, owning responsibility for their correctness/authenticity: a) Bid Security should be furnished i) In the form of DD in favour of Pay Officer/TSSPDCL/ Hyderabad (or) Alternatively BG from Nationalized/Scheduled bank in favor of Chief General Manager/P&MM/TSSPDCL/Hyd as per format-II enclosed (or ) ii) If exempted give details of Bid Security Exemption (in case of Govt. Organization) b) Quantity offered c) Proof of manufacturer-SSI, Department of Industries, Govt. of India Enterprise etc d) Latest “Sales Tax Clearance Certificate” e) Financial Turnover certified by CA for last 5 years f) Details of previous supplies along with PO copies and delivery challan copies for qualification requirement as per tender document. g) Performance Certificates issued by Head of Purchasing Authority (as per spec) h) Copies of relevant purchase order copies mentioned in the performance certificates in support of the above. i) Drawings, Guaranteed Technical Particulars of the product, other relevant documents attached to the bid. j) BIS certificate k) ISO certification l) Type Test Certificates in full shape m) Duly filled and signed proforma as per Format A 6. The rates should be quoted in online only |
|  |  | 7. After uploading the documents the copies of the uploaded statement, certificates, documents, original Demand Drafts in respect of processing fee, testing charges and Bid Security (except the Price bid/offer/break-up of taxes) are to be submitted by the bidder to the Chief General Manager/ P&MM/ TSSPDCL so as to reach before the date and time of opening of the technical bid. Failure to furnish any of the uploaded documents, certificates, before the date and time of opening of technical bid will entail in rejection of the bid. The Department shall not hold any risk on account of postal delay. Similarly, if any of the certificates, documents, etc., furnished by the tenderer are found to be false / fabricated / bogus, the bidder will be disqualified, blacklisted, action will be initiated as deemed fit and the Bid Security will be forfeited. 8. The department will not hold any risk and responsibility regulating non-visibility of the scanned and uploaded documents. 9. The Documents that are uploaded online on e-market place will only be considered for Technical Bid Evaluation. 10. Important Notice to Contractors, Suppliers and Department users (i) In the endeavor to bring total automation of processes in e-Procurement, the Govt. has issued orders vide G.O.Ms.No. 13 dated. 5.7.2006 permitting integration of electronic Payment Gateway of ICICI/HDFC Banks with eProcurement platform, which provides a facility to participating suppliers/ contractors to electronically pay the transaction fee online using their credit cards. |
| 26 | Rights reserved with the Department | TSSPDCL reserves the right to accept or reject any or all of the tenders received without assigning any reasons therefore. The TSSPDCL also reserves the right to split the tender and place orders on more than one tenderer at its discretion |
| 27 | General Terms and Conditions | As per tender documents. |

SECTION - II

SALIENT FEATURES OF THE BID

Superscription on the Tender Cover

Specification No				: STN-746/21

Material				: Three phase, Electronic meter with

net-metering features in PP Box (class 1.0             accuracy)

Officer to whom the bid will be addressed	: CGM/P&MM, Corporate Office/TSSPDCL/Hyd

Superscription on the bid cover and

the outer envelope				:

- Specification No.		                : STN-746/21

- Due date and time for online

& hard copy submission                   :  04-08-2021   at 12:00 Hrs

- Date and time of online opening    :  04-08-2021 at 15:00 Hrs

- Payment of bid security

i) If paid give details: DD No._____Dt.___ for Rs.______

ii) If exempted give details

- Payment of testing charges DD No._____Dt.___ for Rs.______

f. Whether 90 days validity offered ………(yes/no).

g. Whether bid is made accepting payment terms Clause….(yes/no).

h. Whether delivery is as per delivery schedule indicated….(yes/no)

i. Whether the sample (if specified) has been enclosed/sent…(yes/no)

j. Whether the quotation is in two parts …. (Yes/no)

Content of Bidding Documents:

The materials / equipment required, bidding procedures, and contract terms are prescribed in the bidding documents as listed below:

        - Notice Inviting Bids.

        - Salient feature of the contract.

        - Standard General terms and conditions of contract.

        - Standard Technical specification and drawings wherever necessary.

        - Qualification Requirements.

        - Schedule of requirements (delivery Schedule)

SAMPLE FORMS.

        - Bid Form

        - Performance Security Form

i.		Manufacturers’ Authorization form

j. 	Performance Statement

k.	Details to be furnished by the Manufacturer (Format-A)

l.	Schedule of Deviations (Technical & Commercial)

The Bidder is expected to examine all instructions, forms, terms and technical specifications in the bidding documents. Failure to furnish all information required by the bidding documents or to submit a bid not substantially responsive to the bidding documents in every respect will be at Bidder's risk and may result in the rejection of its bid.

Deviations from standard bidding document

i)	General terms and Condition of Contract

ii)	Technical

The above deviations supercede the existing terms of GCC and Technical Specification

Chief general manager (P&MM)

TSSPDCL

SECTION - III

GENERAL TERMS AND CONDITIONS OF CONTRACT

A. Introduction

- Definitions

In this Contract, the following terms will be interpreted as indicated:

- "The Contract" means the agreement entered into between the Purchaser and the Supplier, as recorded in the contract Form signed by the Parties, including all attachments and appendices thereto and all documents incorporated by reference therein.

- "The Contract Price" means the price payable to the Supplier under the Contract for the full and proper performance of its contractual obligations.

(c)	"The Materials / equipment" means all of the equipment, machinery, and/or other materials which the Supplier is required to supply to the Purchaser under the Contract.

(d)	"The Services" means those services ancillary to the supply of the Materials / equipment, such as transportation and insurance, and any other incidental Services, such as installation, commissioning, provision of technical assistance, training, and other such obligations of the Supplier covered under the Contract.

(e)	"GCC" means the General Terms and Conditions of Contract contained in the section.

- "The Purchaser" means the organization purchasing the Materials / equipment.

- Vendor is a supplier who has registered with the purchaser for supply of materials/equipment.

(h)	"The Supplier" means the firm supplying the Materials / equipment and Services under this Contract.

(i)	"Day" means calendar day.

2.	Applicability

These General Conditions of contract will apply to the extent that they are not superseded by provisions of Salient features of the Bid.

3(a)	Standards

The Materials / equipment supplied under this Contract will conform to the Standards mentioned in the Technical specifications, and, when no applicable standard is mentioned, the authoritative standards appropriate to the Materials / equipment' i.e., BIS, such standards will be the latest. All material will be of the best class and will be capable of satisfactory operation under tropical conditions without distortion or deterioration.

3(b)	Interchangeability:

All similar materials and removable parts of similar equipment will be interchangeable with each other.  A specific confirmation of this should be furnished in the bid.

4. 	Scope of Work:

This specification covers design manufacture, testing and delivery FADS (Free At Destination Stores) of the materials described at Section V and Technical Specification Section VI.

5.	Eligible Bidders:

All the Manufacturers who have registered themselves with department of industries of State/Central Govt. with full manufacturing and testing facilities for supply of the material / equipment listed in Section No. V, of Bid specification and meeting the qualification requirements described at section IV and having BIS certification for the items quoted only need quote. Bids received from firms not meeting the above criteria will not be considered.

- THE BIDDING DOCUMENTS

6.	Contents of Bidding Document:

6.1	The Materials / equipment required, bidding procedures, and contract terms are prescribed in the bidding documents as listed below:

- Notice Inviting Bid

- Technical Specifications

- Schedule of Requirements (Delivery Schedule)

- Bid Form and Price Schedules(online only)

- Salient Features of the Bid

- General Terms and Conditions of Contract

- Qualification Requirements

- Bid Security

- Performance Security Form

- Schedule of Deviations

6.2	The Bidder is expected to examine all instructions, forms, terms and Technical specifications in the bidding documents. Failure to furnish all information required by the bidding documents or to submit a bid not responsive to the bidding documents in every respect will be at Bidder's risk and may result in the rejection of its bid.

7.	Clarification of Bidding Documents

Clarification of Bidding Documents: 	A prospective Bidder requiring any clarification of the bidding documents may notify the Purchaser in writing or by cable (hereinafter, the term cable is deemed to include telex and facsimile) at the Purchaser's address. The Purchaser will respond in writing to any request for clarification of the bidding documents, which it receives no later than fifteen (15) days prior to the deadline for the submission of bids. Written copies of Purchaser's response (including an explanation of the query but without identifying the source of inquiry) will be put on Website of the purchaser and e-procurement website or intimated by mail.

8.	Amendment to Bidding Documents:

8.1	At any time prior to the deadline for submission of bids, the Purchaser, for any reason, whether at its own initiative or in response to a clarification requested by a prospective Bidder, may modify the bidding documents by amendment.

8.2	All such amendments also would be made available on the website of TSSPDCL and                e-procurement website and such amendments will be binding on the respective Bidders.

8.3	In order to allow prospective Bidders reasonable time in which to take the amendment into account in preparing their bids, the Purchaser, at its discretion, may extend the deadline for the submission of bids.

### C. PREPARATION OF BIDS

9.	Language of Bid:

The bid prepared by the Bidder including all correspondence and documents relating to the bid exchanged by the Bidder and the Purchaser, will be in English.

10.	Cost Associated with Bidding:

The Bidder will bear all costs associated with the preparation and submission of its bid, and the Purchaser, will in no case be responsible or liable for those costs, regardless of the conduct or outcome of the bidding process.

11.	Documents Constituting the Bid:

The bid prepared by the Bidder will comprise the following components:

    - Bid Security in accordance with Clause No.19.

    - A Bid Form and Price Schedule (only for online submission) completed in accordance with Clause No.12 and 13.

    - Documentary evidence establishing in accordance with Clause No.18 that the Bidder is eligible to bid and is qualified to perform the contract if its bid is accepted.

    - Documentary evidence establishing that the Materials / equipment and ancillary services to be supplied by the Bidder are as per the Technical specification of the bidding documents; and

    - Tax clearance certificate

    - Schedule of Deviations

(a) Commercial

(b) Technical

All the Schedules will be duly filled but not necessary in the sheets attached to the specification unless full details required in the schedules are furnished the Bids will be liable for rejection.

12.	Bid Form:

The Bidder will complete the Bid form and the appropriate Price Schedule (only for online submission) furnished in the bidding documents, indicating the Materials / equipment to be supplied, a brief description of the Materials / equipment, quantity and prices.

13. 	Bid Prices:

13.1	The prices quoted shall be FIRM. Bids will be called for with prices FADS inclusive of packing and forwarding GST and other legally permissible duties and levies wherever applicable, handling charges to cover the transport by road from destination railway station to site/stores and insurance (transit and storage at site for 45 days).

13.2	Even though composite price is given the break-up for all the duties, taxes, freight, insurance, packing and forwarding etc., shall be furnished.

13.3	It is the responsibility of the Bidder to inform himself of the correct rates of duties and taxes leviable on the materials at the time of bidding.

13.4	The proforma credit available to the bidder on the purchases of inputs (raw materials) consequent to the introduction of “MODVAT” Scheme may be taken into account while quoting the prices.

13.5	The Bidder shall indicate on the appropriate Price Schedule (online submission) the unit prices (where applicable) and total bid price of the Materials / equipment it proposes to supply under the contract.

Prices indicated on the price schedule (online) shall be entered separately in the following manner.

The price of the Materials / equipment quoted EXWORKS and all excise and other duties and sales and other taxes payable on the finished Materials / equipment with individual breakup for Taxes and Duties, packing and forwarding, freight and insurance etc.

14.     Taxes and Duties

14.1   	A bidder will be entirely responsible for quoting the correct taxes and duties, other local taxes or levies if any, license fees, etc., he has to incur until completion of the contract. For the purpose of evaluation the bidder should clearly indicate the GST and any other levies payable. Failure to furnish such details leads to loading as indicated in the evaluation criteria.

14.2	If the rates of statutory levies assumed by the Bidder are less than the actual rates prevailing at the time of bidding, the Purchaser will not be responsible for such errors.  If the rates of statutory levies assumed by the Bidder are later proved to be higher than the actual / correct rates prevailing at the time of bidding, the difference will be passed on to the credit of the Purchaser.

14.3.	Deemed Export Benefits: This is not applicable for local purchases with TSSPDCL funds.

15.     	Statutory Variations

In case of subvendor items Taxes, Duties are inclusive in tender price. No statutory variation is applicable. Further price variations in respect of Sub-vendor items will be considered on tender prices.

Any variation up or down in statutory levy or new levies introduced after signing of the contract under this specification will be to the account of TSSPDCL provided. In cases where delivery schedule is not adhered to by the supplier and there are upward variation / revision after the agreed delivered date, the supplier will bear the impact of such levies and if there is downward variation / revision the TSSPDCL will be given credit to that extent. This is allowed only once during delivery period i.e. at the time of delivery of goods at factory.

16. 	Bid Currencies:

Prices shall be quoted in Indian Rupees; and will be paid in Indian Rupees Only.

17.	Quantity to quote:

Bidder shall quote a minimum quantity of at least 20% of the total quantity indicated in the bid Specification. Offers less than the minimum prescribed are liable for rejection.

18.	Documents Establishing Bidder’s Eligibility and Qualifications

The Bidder shall furnish, as part of its bid, documents establishing the Bidder's eligibility to bid and its qualifications to perform the contract if its bid is accepted.

The documentary evidence of the Bidder's qualifications to perform the contract if its bid is accepted will establish to the Purchaser's satisfaction:

(a)   That the Bidder has the financial, technical, and production capability necessary to perform the contract;

(b)	That the Bidder meets the qualification criteria listed in Section VI.  In addition the Bidder may furnish full particulars regarding supply of the material in question made so far to TSSPDCL during the last 5 years and other reputed utilities.

18.1 	Documents Establishing Materials/equipment Conformity to Bidding Documents.

The Bidder shall furnish as part of its bid, documents establishing conformity to the bidding documents of all Materials / equipment and services, which the Bidder proposes to supply under the Contract.

The documentary evidence of conformity of the Materials / equipment and the services to bidding documents may be in the form of literature, drawings, and data, and will consist of:

(a) a detailed description of the essential technical and performance characteristics of the Materials / equipment;

(b)	The bidder should specifically mention about furnishing the test certificates and a specimen form of test certificate should be furnished along with the bid.

(c)	a list giving full particulars, including available sources and current prices of spare parts,  special tools etc., necessary for the proper and continuing functioning  of the Materials / equipment following commencement of the use of the Materials / equipment by the Purchaser; and

(d)	an item-by-item commentary on the Purchaser's Technical Specifications demonstrating substantial responsive-ness of the Materials / equipment and services to those specifications, or a statement of deviations and exceptions to the provisions of the Technical Specifications.

For purposes of the commentary to be furnished pursuant to above, the Bidder will note that standards for workmanship, material, and equipment, as well as references to brand names or catalogue numbers designated by the Purchaser in its Technical Specifications, are intended to be descriptive only and not restrictive. The Bidder may substitute alternative standards, brand names, and/or catalogue numbers in its bid, provided that it demonstrates to the Purchaser's satisfaction that the substitutions ensure substantial equivalence to those designated in the Technical Specifications.

19.	Bid Security

19.1	The Bidder shall furnish, as part of its bid, a Bid Security in the amount of 2% of the Total Ex-works value of the materials offered against the bid (plus with GST @18%).  This amount should be paid by way of a crossed demand draft drawn on any schedule bank in favour of the Pay Officer, TSSPDCL and payable at headquarters of the Purchaser. The crossed DD should invariably be furnished along with the bids.  Alternatively the bidders may furnish a B.G. in original in lieu of DD as per the proforma attached. Fax / photocopies of the bid security will not be accepted and will be rejected.

19.2	The fact of having enclosed bid security by DD/B.G. along with the bid should be clearly super scribed on the bid envelope. Bids, which do not have the above superscription, will be rejected and returned to the respective bidders unopened.

19.3	Submission of BID SECURITY by way of Cheque, cash, money order, call deposit will not be accepted and will be considered as disqualification.

19.4	Payment of BID SECURITY will be waived at the discretion of the TSSPDCL in the case of fully owned Government undertaking of the Central or State Government.  Such undertakings should immediately apply and obtain exemption before submitting their Bids. They need only refer to the details of such exemption in their Bids. Exemption accorded by any organization other than TSSPDCL will not be considered.

19.5	Requests for exemption from payment of BID SECURITY will not be entertained in any other case.

19.6	Any bid not secured as above will be rejected by the purchaser.

19.7	Unsuccessful Bidders' Bid Security will be discharged or returned as promptly as possible, but not later than thirty (30) days after the expiry of the period of bid validity prescribed by the Purchaser.

19.8	The successful Bidder's Bid Security will be discharged upon the Bidder signing the contract.

19.9		The Bid Security may be forfeited:

(a)	if a Bidder:

    - Withdraws its bid or alters its prices during the period of bid validity specified by the Bidder on the Bid Form, or

    - Does not accept the correction of errors pursuant to Clause No.30.2; or

    - Offers post Bid rebates, revisions or deviations in quoted prices and / or conditions or any such offers which will give a benefit to the Bidder over others will not only be rejected outright but the original Bid itself will get disqualified on this account and the Bidder’s BID SECURITY will be forfeited.

(b)	In the case of a successful Bidder, if the Bidder fails:

    - To sign the contract in accordance with Clause No.37.

    - To furnish performance security in accordance with Clause No.38.

19.10	In cases where the Bid Cover Contains superscription of having furnished Bid Security by way of DD but if the same is not found within, such Bids will be rejected and bidder will run the risk of being banned.

Note : 	The bidder shall furnish required Bid Security amount and validity (The validity of the bank guarantee shall be upto bid validity +45 days from the date of tender opening ) as per specification.  If the bidder fails to furnish bid security amount and bid validity as stipulated in the specification, such tender bid will not be considered for further evaluation.

20.		Period of Validity of Bids.

20.1	Bids shall remain valid for the period of Ninety  (90) days from the date of bid opening prescribed by the Purchaser. A bid valid for a shorter period will be rejected.

The bidders should clearly super scribe on the sealed envelopes of the bids about the validity. Bids not containing superscription of validity will be rejected and returned unopened.

20.2	In exceptional circumstances, the Purchaser may solicit the Bidder's consent to an extension of the period of validity. The request and the responses there to will be made in writing (or by cable).  The Bid Security provided under Clause No.19 will also be suitably extended. A Bidder may refuse the request without forfeiting its Bid Security.

21. 	Tax Clearance Certificates:

Copies of Income Tax, Sales Tax and Turnover Tax certificates for the latest period from the appropriate authority will invariably be enclosed to the bid.  In the case of proprietary or partnership firm it will be necessary to produce the certificate / certificates for the proprietor or proprietors and for each of the partners as the case may be.  If the Bidder has already produced the certificate during the calendar year in which the bid is made, it will be sufficient, if particulars are given.

22.	Service Conditions

22.1	The equipment / materials offered will be entirely satisfactory for operation under the climatic conditions indicated below:

(a)	Maximum ambient air temperature (in shade)		450   C

(b)	Maximum ambient air temperature (under sun)		500   C

(c)	Maximum daily average ambient air temperature		350   C

(d)	Maximum yearly average ambient air temperature 		300   C

(e)	Maximum humidity 						100%

(f)	Altitude above M.S.L.						Up to 1000M

(g)	Average No. of thunder storm days per annum		50

(h)	Average No. of dust storm days per annum	             		Occasional

(i)	Average No. of rainy days / annum				90

(j)	Average Annual Rain fall 					925mm

(k)	Normal tropical monsoon period				4 months

(l)	Maximum wind pressure					150 kg/Sq.M.

22.2	Due consideration will be given to any special devices or attachments put forward by the Bidder which are calculated to enhance the general utility and the safe and efficient operation of the equipment / materials.

23.       Format and Signing of Bid.

23.1	The Bidder shall seal the original bid, duly marking envelope as "ORIGINAL". The envelopes will then be sealed in an outer envelope.

23.2	The original and the copies of the bid shall be typed and shall be signed by the Bidder or a person or persons duly authorized to bind the Bidder to the contract.  The person or persons signing the bid will initial all pages of the bid, except for printed literature.

23.3   	Any interlineations, erasures, or overwriting will be valid only if they are initialed by the person or persons signing the bid.

###### D. Submission of Bids

24.      Submission, Sealing and Marking of Bids.

  - The tenderers are required to submit their bids in two parts as under:

(i)	Part-I	:	Bid Security, Technical Bid & Qualification Requirements. Technical Bid shall contain full technical    particulars and commercial terms and conditions but without prices. This should not contain any cost information whatsoever.

Part-II 	:	Price Bid – containing Prices (shall be on-line only)

Bids received with any details pertaining to prices in the offline mode will be liable for rejection.

(ii)	The Part-I of tender should be furnished in a sealed cover super scribing tender enquiry number, name of material, name of the bidder and date of tender opening

(iii)	Part-I of the bid will be opened on the due date of tender opening.  In case the bidders have been granted Bid Security exemption (clause-19), documentary evidence for the same must be furnished.  The firms whose Bid Security, Testing charges and Transaction Fee are not received as specified in the tender document, the price bids will not be opened and their bids will be rejected summarily.

(iv)	The price bids of only those bidders whose technical bids, on examination, are determined to be technically and commercially acceptable and meeting the specified Qualification Criteria will be opened at a later date.

Sealing and Marking of Bids.

24.2  	The Bidder shall seal the bid in an envelope.

24.3    The inner and outer envelopes will be  addressed to the purchaser.

24.4    The sealed cover as well as the outer envelope should be super scribed as follows:

- Bid Enquiry No.

- Due date and time for hard copy and online submission.

- Date and time for online opening.

- Payment of Bid Security

(i)     If paid, give details: D.D. No……. Date: ……..

- Whether 90days validity offered……….YES / NO

- Payment of testing charges D.D. No……. Date: ……..

- Whether the quotation is made accepting Payment terms clause …. YES/NO

- Whether the delivery is as per delivery schedule indicated…. YES/NO

- Whether the sample (if specified) has been enclosed/ sent…YES/NO

- Whether the bid is quoted in two parts (clause 24.1)…. (YES/NO)

  - Bids not super scribed as above are liable to be rejected.

24.6 	The Bidder shall invariably complete the Bid in full. Details to be furnished by the bidder and Schedule of Prices attached to the specification and enclose the same to the bid without fail.

24.7	The bids shall be in bound volumes (With the documents in the volume not detachable). All pages of the bid except in-amended printed literature shall be initiated by the person/persons signing the bid. The page number shall be referred in Index. All pages including literature, type test reports of the bid shall be numbered and the page numbers shall be continuous. Soft copy of the technical and commercial bids and designs with drawings shall be given in Floppy disc/ CD also. Summary sheet in the given format on the top of the bid duly signed and sealed by the bidder.

24.8	The time of actual receipt in the office only will count for the acceptance of the bid and either the date of bid, date stamp of post office or date stamp of any other office will not count. The TSSPDCL will not be responsible for any postal or any other transit delays.

24.9	Telegraphic quotations will not be entertained under any circumstances. Clarification, amplifications, and/or any other correspondence from the Bidder subsequent to the opening of bid will not be entertained.  The Bidders are advised to ensure that their bids are sent in complete shape at the first instance itself.

24.10	The inner envelopes shall also indicate the name and address of the Bidder to enable the bid to be returned unopened in case it is declared "late".

24.11	If the outer envelope is not sealed and marked as required above, the Purchaser will assume no responsibility for the bid's misplacement or premature opening.

25. 	Deadline for Submission of Bids.

25.1	Bids together with modifications if any, or other withdrawals must be received by the Purchaser not later than the deadline for submission of bids specified in the Salient features of the Bid.

25.2	The Purchaser may, at its discretion, extend this deadline for the submission of bids by amending the bidding documents in which case all rights and obligations of the Purchaser and Bidders previously subject to the deadline will thereafter be subject to the deadline as extended.

26.       Late Bids

26.1	Any bid received by the Purchaser after the deadline for submission of bids prescribed by the Purchaser will be rejected and returned unopened to the Bidder.

26.2     Modification and Withdrawal of Bids.

The Bidder may modify or withdraw its bid after the bid's submission, provided that written notice of the modification, including substitution or withdrawal of the bids, is received by the Purchaser prior to the deadline prescribed for submission of bids.

The Bidder's modification or withdrawal notice will be prepared, sealed, marked, and dispatched. A withdrawal notice may also be sent by cable, but followed by a signed confirmation copy, postmarked not later than the deadline for submission of bids. No bid may be modified after the deadline for submission of bids.

No bid may be withdrawn in the interval between the deadline for submission of bids and the expiration of the period of bid validity specified. Withdrawal of a bid during this interval may result in the forfeiture of its Bid Security.

###### E. 	Opening and Evaluation of Bids

27.       Opening of Bids by the Purchaser

27.1	The Purchaser will open all bids meeting above criteria at the time, on the date, and at the place specified.

27.2   	The Bidders' names, bid modifications or withdrawals, discounts and the presence or absence of requisite Bid Security and such other details as the Purchaser, at its discretion, may consider appropriate, will be announced at the opening.

27.3  	Bids that are not opened at bid opening will not be considered further for evaluation, irrespective of the circumstances.

28.	     Clarification of Bids

During evaluation of the bids, the Purchaser may, at its discretion, ask the Bidder for a clarification of its, bid.  The request for clarification and the response shall be in writing, and no change in the prices or substance of the bid shall be sought, offered, or permitted.

29.	    Preliminary Examination

29.1	The Purchaser will examine the bids to determine whether they are complete, whether any computational errors have been made, whether required sureties have been furnished, whether the documents have been properly signed, and whether the bids are generally in order.

29.2 	Arithmetical errors will be rectified on the following basis. If there is a discrepancy between the unit price and the total price that is obtained by multiplying the unit price and quantity, the unit price will prevail, and the total price will be corrected.  If the Supplier does not accept the correction of the errors, its bid will be rejected, and its Bid Security may be forfeited.  If there is a discrepancy between words and figures, the amount in words will prevail.  If the supplier does not accept the correction of the errors, its bid will be rejected and its Bid Security may be forfeited.

29.3 	The Purchaser may waive any minor informality, nonconformity, or irregularity in bid which does not constitute a material deviation, provided such waiver doesn't prejudice or affect the relative ranking of any Bidder.

29.4  	Prior to the detailed evaluation, the Purchaser will determine the substantial responsiveness of each bid to the bidding documents.  For purposes of these Clauses, a substantially responsive bid is one, which conforms to all the terms and conditions of the bidding documents without material deviations. Deviations from, or objections or reservations to critical provisions, such as those concerning Bid Security, and Taxes and Duties will be deemed to be a material deviation.  The Purchaser's determination of a bid's responsiveness is to be based on the contents of the bid itself without recourse to extrinsic evidence.

29.5  	If a bid is not substantially responsive, it will be rejected by the Purchaser and may not subsequently be made responsive by the Bidder by correction of the nonconformity.

Note :		Payment terms, Delivery period, Performance Bank Guarantee, Taxes and Duties” 	should be in line with the terms and conditions of the specification. If any bidder 	does not meet any one of the conditions, such tender will not be considered. Please 	note that the conditional offers are also not considered. Hence the bidder shall 	submit the tender in line with the terms and conditions of the specification.

30.	Evaluation and Comparison of Bids.

30.1	The Purchaser will evaluate and compare the bids, which have been determined to be substantially responsive.

30.2	The Purchaser's evaluation of a bid will take into consideration one or more of the following factors

All the bids, which are opened, read out and considered for evaluation, will be checked for qualification requirements in respect of technical and commercial aspects. Such of the bids, which do not meet the qualification requirements, will not be evaluated further. The bid is to be checked for its conformity to the technical specification. If it does not meet the technical specification, the Bid will not be evaluated further. However, if in the opinion of the purchaser the bidder has offered equipment / material better than the technical specification the same may be considered. The bid may be rejected for the following reasons:

1.   Not in the prescribed form

- Insufficient bid security or bid not accompanied by the required bid security or proof of exemption.

- Bids not properly signed

- The bidder is a vendor who is banned from further business transactions and the period of ban is still in force.

- Bid received after the due date and time

- The bid is through telegram or fax

- Further, the purchaser may enquire from the bidder in writing for any clarification of the bid. The response of the bidder will also be in writing. However no change in the prices or substance of the bid will be sought, offered or permitted.

- Bids will be examined for completeness and for any computational errors.

- Arithmetical errors will be rectified on the following basis.

  - Where there is a discrepancy between the unit price and total price, the unit price will prevail and the total price will be corrected accordingly.

  - Where there is a discrepancy between words and figures, the amount in words will prevail.

  - Failure on the part of the bidder to agree to the above corrections will result in rejection of his offer and forfeiture of his bid security.

- It will be ensured that the required sureties have been furnished and that the documents have been properly signed.

- The purchaser's evaluation of a bid will take into consideration one or more of the following factors

(a)	Delivery schedule offered in the bid;

(b)	Deviations in payment schedule from that specified in the general terms and conditions of the contract and technical deviations.

(c)	The cost of components, mandatory spare parts, and service;

(d)	The availability of spare parts and after-sales services for the equipment offered in the Bid;

(e)	The projected operating and maintenance costs during the life of the equipment;

(f)	The performance and productivity of the equipment offered;

(g)	Other specific criteria indicated in the Bidding documents.

In addition the Purchaser’s evaluation of a bid will take into account the net landed cost of the material at the final destination. For the purpose of evaluation net landed cost is arrived at by adding all elements of the basic price, allowable discount, excise duty & any other levies, packing & forwarding, freight charges, insurance (transit & storage) as quoted by the bidder, interest on advance if any, erection, servicing  other charges and inclusive of GST  as called for.

In addition any variation up or down in taxes and duties / new levies introduced subsequent to bid opening and before award will be considered for comparison purposes.

The following criteria may be adopted for taxes and duties for evaluation

a.     It is the responsibility of the bidder to quote all taxes and duties correctly without leaving any column unfilled. Where taxes and duties are not applicable the bidder should enter “NA”.  If no duty / tax is le-viable the same may be entered as “NIL”. If any column is left blank or filled vaguely like “as applicable”, the same will be loaded with the maximum of the other eligible Bids.

  - Where there is an exemption of GST, the documentary evidence to that effect will be enclosed by the supplier.

c.	The bidders for supply and works shall invariably possess the GSTIN number and PAN Number for the bids above Rs. 5.00 lakhs and this must be verified before entering into contract.

- Prior to detailed evaluation, the responsiveness of each bid will be determined. A substantially responsive bid is one that conforms to all the terms and conditions of the bidding documents without material deviations. For this purpose superscription, qualification requirement, bid security, validity, delivery, payment term, price schedule, taxes and duties will be deemed to be the critical provisions and deviations in any one of these items will be deemed to be a material deviation.

The purchaser may waive any minor informality, non-conformity or irregularity in the bid which does not constitute a material deviation, provided such waiver does not affect the relative ranking of any bidder.  The purchaser will clearly indicate in the bid specification the methodology for evaluation of bids.

(a)	Bid price, which will include all, costs of manufacture and services at manufacturing place as well as, Transportation to destination stores, packing and forwarding, insurance and all Taxes & other legally permissible duties& levies payable.

(b)	Delivery schedule offered in the bid.

(c)	Deviations in payment schedule from that specified in the general terms and conditions of the contract.

(d)	The cost of components, mandatory spare parts, and service

(e)	The availability of spare parts and after-sales services for the equipment offered in the Bid;

(f)	The projected operating and maintenance costs during the life of the equipment;

(g)	The performance and productivity of the equipment offered; and/or

- Other specific criteria indicated in the Bid Specification.

30.3(a) The Purchaser’s evaluation of a bid will take into account the Net Landed Cost of the Material at destination stores inclusive of all taxes and duties and inclusive of GST quoted by the Bidder.  It is the responsibility of the bidder to quote all Taxes and Duties correctly without leaving any column unfilled.  Where not applicable the column may be filled as “NA”.  If no duty / tax is le-viable the same may be filled as “NIL”. If any column is left blank the same is loaded with maximum of other eligible Bids.

30.3(b) Any statutory variations of taxes and duties and new levies imposed after opening of the bid and before award of the contract will be taken into consideration for the purpose of evaluation.

30.4	A substantially responsive bid is one, which conforms to all the terms and conditions of the bidding documents without material deviations. For this purpose superscription, qualification requirement, bid security, validity, delivery, payment term, price schedule, submission of Types test certificates (as per Clause 4 section VI), taxes and duties will be deemed to the critical provisions and deviations in any one of these things will be deemed to be a material deviation.

31.	Contacting the Purchaser.

31.1	From the time of the bid opening to the time of contract award, if any Bidder wishes to contact the Purchaser on any matter related to the bid, it should do so in writing.

31.2	Any effort by a Bidder to influence the Purchaser in its decisions on bid evaluation, bid comparison, or contract award will result in the rejection of the Bidder's bid.

F. 	Award of Contract.

32.       Post Qualification

32.1	In the absence of pre-qualification, the Purchaser will determine to its satisfaction whether the Bidder that is selected as having submitted the lowest evaluated responsive bid is qualified to perform the contract satisfactorily.

32.2  	The determination will take into account the Bidder's financial, and production capabilities.  It will be based upon an examination of the documentary evidence of the Bidder's qualification submitted by the Bidder, as well as such other information as the Purchaser deems necessary and appropriate.

33.	Award Criteria:

The Purchaser will award the contract to the successful Bidder / Bidders whose bid has / have been determined to be substantially responsive.

However it is not binding on TSSPDCL to accept the lowest or any other Bid.  It reserves the right to place orders on different Bidders.

34.	Purchaser’s Right to Vary Quantities at Time of Award

34.1	The Purchaser reserves the right at the time of contract award to increase or decrease the quantity by +/- 50%of Materials / equipment and services originally specified in the Schedule of Requirements without any change in unit price or other terms and conditions.

34.2	The purchaser reserves the right to vary the ordered quantity by +/- 50% during the execution of the contract.

35.	Purchaser's Right to Accept Any Bid and to Reject Any or All Bids

The Purchaser reserves the right to accept or reject any bid, and to annul the bidding process and reject all bids at any time prior to contract award, without thereby incurring any liability to the affected Bidder or Bidders or any obligation to inform the affected bidder or bidders.

36.	Notification of Award

36.1	Prior to the expiration of the period of bid validity, the Purchaser will notify the Successful Bidder in writing by registered letter or by cable, to be confirmed in writing by registered letter, that its bid has been accepted.

36.2	The notification of award will constitute the formation of the Contract.

36.3  	Upon the successful Bidder's furnishing of the performance security, the Purchaser enters into contract with successful Bidder / Bidders. The Purchaser will notify each unsuccessful Bidder and will discharge its Bid Security.

37.	Signing of Contract:

The Purchaser notifies the successful Bidder that its bid has been accepted.

Within 30 (thirty days) of receipt of notification of award of Contract, the successful Bidder will sign and date the contract. Failure to comply with this stipulation will entail cancellation of the contract besides forfeiture of the bid security.

38.	Performance Security:

38.1   	Within Fifteen (15) days of receipt of the notification of Contract award. The successful Bidder will furnish to the Purchaser the performance security for an amount 10% of the contract value for proper fulfillment of the contract, which will include the warranty period, and completion of performance obligations including Warranty obligations. The Performance Security will cover 60 days beyond the date of completion of performance obligations including Warranty obligations.

In the event of any correction of defects or replacement of defective material during the warranty period, the warranty for the corrected / replaced material will be extended to a further period of 12 months and the Performance Bank Guarantee for proportionate value will be extended 60 days over and above the extended warranty period.

38.2  	 The proceeds of the performance security will be payable to the Purchaser as compensation for any loss resulting from the Supplier's failure to complete its obligations under the Contract.

38.3 	The performance security will be…

- A bank guarantee issued by a Nationalized bank or scheduled bank acceptable to the Purchaser, in the form provided in the bidding documents.

- A banker's cheque or crossed DD or Pay Order payable at the Head quarter of    the Purchaser in favour of the Purchaser drawn on any scheduled bank.

38.4   	The performance security will be discharged by the Purchaser and returned to the Supplier not later than sixty (60) days after the expiry date.

38.5   Failure of the successful Bidder to comply with the above requirement will entail cancellation of the award and forfeiture of the Bid Security and the balance to make up the performance security deposit will be deducted form pending payments if any due to the tenderer form TSSPDCL on other orders in addition the company will also become liable for being black listed by TSSPDCL.

39.	Corrupt or Fraudulent Practices

It is essential that the Purchaser as well as Bidder/supplier / contractor for the purposes of this provision, the terms set forth below as follows:

(i) “Corrupt practice” means the offering, giving, receiving or soliciting of any thing of value to influence the action of a public official in the procurement process or in contract execution, and

(ii) “Fraudulent practice” means a misrepresentation of facts in order to influence a procurement process or the execution of a contract to the determinant of the purchaser, and includes collusive practice among Bidders (prior to or after bid submission) designed to establish bid prices at artificial non-competitive levels and to deprive the purchaser of the benefits of free and open competition;

(iii) Will reject a proposal for award if it determines that the Bidder recommended for award has engaged in corrupt or fraudulent practices in competing for the contract in question;

(iv) Will declare a firm ineligible, either indefinitely or for a stated period of time, to be awarded a contract if it at anytime determines that the firm has engaged in corrupt or fraudulent practices in competing for, or in executing, a contract.

40.	Use of Contract Documents and Information:

40.1	The Supplier will not, without the Purchaser's prior written consent, disclose the Contract, or any provision thereof, of any specification, plan, drawing, pattern, sample, or information furnished by or on behalf of the Purchaser in connection therewith, to any person other than a person employed by the Supplier in the performance of the Contract.  Disclosure to any such employed person will be made in confidence and will extend only so far as may be necessary for purposes of such performance.

40.2	The Supplier will not, without the Purchaser's prior written consent, make use of any document or information except for purposes of performing the Contract.

40.3	Any document, other than the Contract itself, will remain the property of the Purchaser and will be returned (in all copies) to the Purchaser on completion of the supplier's performance under the Contract if so required by the Purchaser.

40.4   	The Supplier will permit the Purchaser or his authorized representative to inspect the Supplier’s accounts and records relating to the performance of the Supplier and to have them audited by auditors appointed by the Supplier.

41.	Patent Rights

The Supplier will indemnify the Purchaser against all third-party claims of infringement of patent, trademark, or industrial design rights arising from use of the Materials / equipment or any part thereof.

42.	Places / Locations:

Particulars of site location and nearest rail heads to which the equipments / material have to be supplied will be given to successful Bidders.

43.	Delivery:

Delivery period will be reckoned from the date of signing of the contract.  The delivery quoted will be firm, definite, unconditional and on the basis of receipt of materials at destination in good condition without any bearing on the procurement of raw materials or any similar prerequisites.  The commencement date and date of delivery will be indicted. The preferred delivery time, which is the essence of this specification, is indicated in the schedule.  Final deliveries are however, subject to confirmation at the time of Contract.  Delay in delivery of materials FADS – (Free At Destination Store) due to non-availability of railway booking, non-allotment of wagons and any such reasons will not be considered.  It is the responsibility of the supplier to make alternative arrangements for transporting the materials by road or rail so as to see that the material reaches the destination within the stipulated period.  The Purchaser reserves its right to defer the delivery date at any time after orders are placed without any change in the conclusion of contract other conditions supply.  The delivery period, which will be reckoned from the date of the Contract, will be guaranteed under penalty as in Clause 61.

44.     Inspections and Tests

(i)  The supplier will keep the Purchaser informed in advance of the time of the   starting and the progress of manufacture of equipment in its various stages so that arrangement could be made for inspection. The accredited representative of the TSSPDCL will have access to the supplier’s or his subcontractor’s work at any time during working hours for the purpose of inspecting the materials during manufacturing of the materials / equipment and testing and may select test samples from the materials going into plant and equipment.  The supplier will provide the facilities for testing such samples at any time including access to drawings and production data at no charge to Purchaser.  As soon as the materials are ready the supplier will duly send intimation to TSSPDCL by Regd. Post and carry out the tests in the presence of representative of the TSSPDCL.

(ii)	The TSSPDCL may at its option get the materials inspected by the third party if it feels necessary and all inspection charges in this connection will be borne by the TSSPDCL. In case of material, not of acceptable quality or not conforming to the specification, the materials will be rejected. The material has to be re-offered for inspection. In such a case the 2nd inspection charges are to suppliers account. In case the materials are rejected in the 2nd inspection also, the TSSPDCL reserves the right to cancel the order.

(iii)  The dispatches will be affected only if the test results comply with the specification.  The dispatches will be made only after the inspection by the TSSPDCL Officer is completed to the TSSPDCL satisfaction or such inspection is waived by the competent authority.

(iv)  The acceptance of any quantity of materials will in no way relieve the supplier of its responsibility for meeting all the requirements of this specification and will not prevent subsequent rejection if such materials are later found to be defective.

(v)  The supplier will give 15 days advance intimation to enable the Purchaser to depute his representative for witnessing the acceptance and routine tests.

(vi) 	Should any inspected or tested materials / equipment fail to conform to the specification, the Purchaser may reject the materials and supplier will either replace the rejected materials or make alterations necessary to meet specifications requirements free of costs to the Purchaser.

(vii) In the case of transformers, instrument transformers and meters inspection will be conducted every year, for the first 5 years on a 2% sample of the quantities supplied.  Samples will be collected at random to establish that the guaranteed technical parameters are as per the submitted bid by the supplier. In the case of non-adherence, the purchaser may take suitable action on the supplier including cancellation of vendor registration and banning further dealings, depending on the gravity of the deviation. These random inspections may be entrusted to a third party.

(viii) Inspection not carried out due to non-readiness of the material even after contacting / confirmed over phone from the supplier about availability of material    and physical verification at the supplier premises, the charges @ 0.3% of Ex-works price of material offered for inspection (inclusive of GST and all other taxes & duties, travelling expenses, boarding and lodging charges at the place of inspection and all incidental charges) shall be paid by supplier subject to a maximum of Rs. 10,000.00

45.	Name Plate:

Equipment should be provided with name plate giving full details of manufacture, capacities and other details as specified in the relevant ISS or other specification stipulated.  The contract No. and date and year of supply and the words “TSSPDCL” must be etched on the name plate.

46.	Packing

46.1	The Supplier will provide such packing of the Materials / equipment as is required to prevent their damage or deterioration during transit to their final destination, as indicated in the Contract. The packing will be sufficient to withstand, without limitation, rough handling during transit and exposure to extreme temperatures, salt and precipitation during transit, and open storage.  Packing case size and weights will take into consideration, where appropriate, the remoteness of the Materials / equipment' final destination and the absence of heavy handling facilities at all points in transit.

46.2   	The packing, marking, and documentation and outside the packages will comply strictly with such special requirements as will be expressly provided for in the Contract and in any subsequent instructions ordered by the Purchaser. The supplier will be required to make separate packages for each consignee; each package will be marked on three sides with proper paint / indelible ink with the following;

- Contract Number

  - Supplier’s name

  - Packing list reference number

46.3 The supplier, whenever dispatches material to a destination should prepare the following information in the form of packing slip in quadruplicate and send the same to the consignee and obtain his acknowledgement. The consignee will return to the supplier one copy of the packing slip with his remarks.  The proforma of packing slip will be as follows:

# PACKING SLIP

- Contract No. & Date.

- Quantity allotted to the stores and rate applicable.

- Quantity so far supplied to the stores and the rate applied.

- Quantity now supplied and the rate applied.

- Total quantity supplied under the Contract with rates applied.

- Programme for supplying the balance quantity to the Stores.

47.        Delivery Documents

47.1	Delivery of the Materials/equipment will be made by the Supplier in accordance with the terms specified in the contract.

The latest test certificates containing the result of the tests as per the relevant ISS or other specification stipulated must be submitted to the Chief General Manager (P&MM) and got approved by him.

47.2	Documents to be submitted by the Supplier are specified as under…

(i)  	Insurance certificate;

(ii)	Supplier’s certificate certifying that the defects if any pointed out during inspection has been rectified (3 copies).

(iii)	Manuals in Six sets and one set of reproducible drawings.

The Purchaser will receive the above documents soon after the dispatch of materials and if not received, the supplier will be responsible for any consequent expenses.

48.     Insurance

    - The Materials / equipment supplied under the Contract will be fully insured against loss or damage incidental to manufacture or acquisition, transportation and delivery and also storage for 45 days at destination stores before taking into account.

    - The bidder shall a) Initiate and pursue insurance claim till settlement, and b) Promptly arrange for repair and/or replacement of any damaged items in full irrespective of settlement of insurance claim by the under Writers. c) All costs because of insurance liabilities covered under the contract will be to supplier’s account. The supplier shall provide the Purchaser with a copy of all insurance policies and documents taken out  by him in pursuance of the ‘Contract’. Such copies of documents shall be submitted to the purchaser immediately after such insurance coverage. The supplier shall also inform the Purchaser in writing at least sixty (60) days in advance, regarding the expiry, cancellation and/or change in any of such documents and ensure revalidation/renewal etc., as may be necessary well in time.

The risks that are to be covered under the insurance shall be comprehensive and shall include but not limited to, the loss or damage in transit, storage, due to theft, pilferage, riot, civil commotion, weather conditions, accident of all kinds, fire, flood, war risk(during ocean transportation) bad or rough handling etc. The scope of such insurance shall cover the entire contract value.

The insurance will be in an amount equal to 100% FADS value of Materials / equipment on all risks basis. The policy will have a provision for extension to cover further storage if necessary at destination stores / site at TSSPDCL cost. The supplier will take the insurance cover in the name of purchaser.

49.	Transportation

The Supplier is required under the Contract to transport the Materials / equipment to a specified place of destination defined as normally the district stores, transport to such place of destination, including insurance and storage, will be arranged by the Supplier, and the related costs will be included in the Contract Price only.

50.       Incidental Services

The Supplier may be required to provide any or all of the following services, including additional services, if any.

(a)	Performance or supervision of on-site assembly and/or start-up of the supplied Materials / equipment;

(b)	Furnishing of tools required for assembly and/or maintenance of the supplied Materials / equipment;

(c)	Furnishing of a detailed operations and maintenance manual for each appropriate unit of the supplied Materials / equipment;

(d)	Performance or supervision or maintenance and/or repair of the supplied Materials / equipment, during warranty period, provided that this service will not relieve the Supplier of any warranty obligations under this contract; and

(e)	Training of the Purchaser's personnel, at the Suppliers' plant and/or on-site, in assembly, start-up, operation, maintenance, and/or repair of the supplied Materials / equipment.

51.  	Spare Parts

The Supplier may be required to provide any or all of the following materials, notifications, and information pertaining to spare parts manufactured or distributed by the Supplier.

        - Such spare parts as the Purchaser may choose to purchase from the Supplier, provided that this election will not relieve the supplier of any warranty obligations under the contract; and

        - In the event of termination of production of the spare parts:

        - Advance notification to the Purchaser of the impending termination.

        - Time to permit the Purchase to procure needed requirement; and following such termination, furnishing at no cost to the Purchaser, the blueprints, drawings, and specifications of the spare parts, if requested.

52.	Warranty

52.1	The supplier will warrant for the satisfactory functioning of the material / equipment as per specification for a minimum period of 5 years from the date of receipt of the material / equipment in good condition.

52.2	The Supplier warrants that the Materials/equipment supplied under the Contract are new, unused, of the most recent or current models and that they incorporate all recent improvements in design and materials unless provided otherwise in the Contract. The supplier further warrants that all Materials/equipment supplied under this Contract will have no defect, arising from a design and /or materials as required by the Purchaser's specifications or from any act of omission of the Supplier that may develop under normal use of the supplied Materials/equipment.

52.3	All the material will be of the best class and will be capable of satisfactory operation in the tropics under service conditions indicated in clause 23.1 without distortion or deterioration.  No welding filling or plugging of defective parts will be permitted, unless otherwise specified, they will conform to the requirements of the appropriate Indian, British or American Standards. (Where a standard specification covering the material in question has not been published, the standards of the American Society for testing of Materials should be followed).

52.4	The entire designs and construction will be capable of withstanding the severest stresses likely to occur in actual service and of resisting rough handling during transport.

52.5	Unless otherwise specified the warranty period will be 5 years from the date of acceptance of the Materials / equipment. The Supplier will, in addition, comply with the performance guarantees specified under the contract.  If, for reasons attributable to the Supplier, these guarantees are not attained in whole or in part, the supplier will at its discretion either, Make such changes, modifications, and/or additions to the Materials / equipment or any part thereof as may be necessary in order to attain the contractual guarantees specified in the contract at its own cost and expense and to carry out further performance tests as per the relevant standards.

52.6	The Purchaser will promptly notify the supplier in writing of any claims arising under this warranty.

52.7  	"Upon receipt of such notice, the Supplier will within 30 days repair or replace the defective Materials/equipment or parts thereof, free of cost at the ultimate destination.  The supplier will take over the replaced parts/Materials / equipment at the time of their replacement.  No claim whatsoever will lie on the Purchaser for the replaced parts/Materials/equipment thereafter". In the event of any correction of defects or replacement of defective material during the warranty period, the warranty for the corrected/replaced material will be extended to a further period of 12 months.

52.8    	If the Supplier, having been notified, fails to remedy the defect(s) within the above period, the Purchaser may proceed to take such remedial action as may be necessary, at the Supplier's risk and expense duly deducting the expenditure from subsequent bills / bank guarantee and without prejudice to any other rights which the Purchaser may have against the Supplier under the Contract.

53.	Payment

“100% payment will be arranged on or after 30 days from the date receipt of 	material/equipment at the destination/stores (i.e.103 entry in SAP module) duly 	transferring the said amount to the bank account of the supplier by the purchaser 	bank. The supplier will have to predefine the Bank details while entering into contract 	for electronic transfer of payments.

Note:

- The date of delivery would be the date on which the stores officer certifies the receipt of materials at stores in good condition 103 entry in SAP module in respective of the date of check measurement.

- Form 13 shall be issued subject to material taken into stock in good condition (i.e. 105 entry in SAP module)

- The supplier should invariably submit test certificates as soon as despatch is made so that the test certificates can be checked up and approved well before it becomes due for payment. Routine Test Certificates of the entire lot shall be submitted to the Consignee.

- The performance guarantee to be executed in accordance with this specification shall be furnished on a stamp value of Rs.100/- The performance guarantee shall be from any Nationalized/Scheduled Bank. Performance Guarantee to the extent of 10% value of purchase order valid upto 2 months over and above the guarantee period to draw 100% payment.

The performance guarantee has to be extended suitably by you in accordance with the guarantee clause, so that the last consignment against the order is covered by the guarantee.

- If you have received any over payments by mistake or if any amounts are due to the TSSPDCL due to any other reason, when it is not possible to recover such amounts under the contract resulting out of the subject specification, the TSSPDCL reserves the right to collect the same from any other amounts and/or bank guarantee given by you due to or with the TSSPDCL.

- When you do not at any time, fulfill your obligations in replacing / rectifying etc., of the damaged/ defective materials in part or whole promptly to the satisfaction of the TSSPDCL officers, the TSSPDCL reserves the right not to accept the bills against subsequent dispatches made by the supplier and only the supplier will be responsible for any demurrages, wharf ages or damages occurring to the consignment so dispatched.

54.     	Prices

Prices charged by the Supplier for Materials / equipment delivered and Services performed under the Contract will not vary from the prices quoted by the supplier in its bid, with the exception of any price adjustment authorized in the contract.

55.	Change Orders

The Purchaser may at any time, by a written order given to the Supplier make changes within the general scope of the Contract   in any one or more of the following:

- Drawings, designs, or specifications, where Materials / equipment to be furnished under the Contract are to be specifically manufactured for the Purchaser;

- The method of shipment or packing;

- The place of delivery; and/or

- The Services to be provided by the Supplier.

56.	Contract Amendments

No variation in or modification of the terms of the Contract will be made except by written amendment by the Purchaser and accepted by the supplier.

57.	Assignment

The Supplier will not assign, in whole or in part, its obligations to perform under this Contract, except with the Purchaser's prior written consent.

58.	Delays in Supplier’s Performance

58.1	Delivery of the Materials / equipment will be made by the Supplier in accordance with the time schedule prescribed by the Purchaser in the Schedule of Requirements.

58.2   	If at any time during performance of the Contract, the Supplier should encounter conditions impeding timely delivery of the Materials / equipment, the Supplier will promptly notify the Purchaser in writing of the fact of the delay, its likely duration and its cause(s). As soon as practicable after receipt of the Supplier's notice, the Purchaser will evaluate the situation and may at its discretion extend the Supplier's time for performance, with or without liquidated damages, in which case the extension will be ratified by the parties by amendment of the Contract.

58.3   	Except as provided under force measure clause a delay by the Supplier in the performance of its delivery obligations will render the Supplier liable to the imposition of liquidated damages unless an extension of time is agreed upon without the application of liquidated damages.

59.		Penalty for delay in supplies

The time for and the dates for delivery mentioned in the contract will be deemed to be the essence of the contract.  Subject to force measure Clause No.64, if the Supplier fails to deliver any or all of the Materials/equipment or to perform the Services within the period(s) specified in the Contract, the Purchaser will, without prejudice to its other remedies under the Contract, deduct from the Contract Price, as liquidated damages, a sum equivalent to 0.5% per week on the undelivered portion subject to a maximum of 5% of the cost of the undelivered portion within scheduled time. Once the maximum is reached the Purchaser may consider termination of the contract.

The check measurement date ie., the date of receipt of materials at destination stores in good condition will be taken as the date of delivery. For calculation of penalty the date of receipt of material at the destination stores is the date of delivery subject to the condition that the goods/material are received in good condition. Materials / Equipment which are not of acceptable quality or are not confirming to the specification would be deemed to be not delivered. For penalty, the number of days would be rounded off to the nearest week and penalty calculated accordingly.

The penalty specified above will be levied and would be adjusted against subsequent pending bills.

In cases where new vendors fail to meet the requirement of the Contract there would be no penalty to such vendors but they will be excluded from the next bid for the particular item of the material.

Any failure on the part of new vendors for a second time would cause them to be removed from the list of registered vendors.

60.    	Risk Purchase

Incase of supplier who has not adhered to the delivery schedule, the TSSPDCL reserves the right to purchase the balance quantity from the open market/floating another tender and recover the extra expenditure thus incurred from the supplier.

61	Termination for Default

61.1	The Purchaser, without prejudice to any other remedy for breach of Contract, by written notice of default sent to the Supplier, may terminate this Contract in whole or in part:

i. If the Supplier fails to deliver any or all of the Materials / equipment within the period(s) specified in   the Contract, or within any extension thereof granted by the Purchaser.

ii.   If the Supplier fails to perform any other obligation(s) under the Contract.

iii. If the Supplier, in the judgment of the Purchaser has engaged incorrupt or

Fraudulent practices in competing for or in executing the Contract.

61.2  	 In the event the Purchaser terminates the Contract in whole or in part, the Purchaser may procure, upon such terms and in such manner, as it deems appropriate, Materials / equipment or services similar to those undelivered, and the Supplier will be liable to the Purchaser for any excess costs for such similar Materials / equipment or Services.  However, the Supplier will continue performance of the Contract to the extent not terminated.

62.	Termination for Insolvency

The Purchaser may at any time terminate the Contract by giving written notice to the Supplier if the Supplier becomes bankrupt or otherwise insolvent. In this event, termination will be without compensation to the supplier, provided that such termination will not prejudice or not affect any right of action or remedy, which has accrued or will accrue thereafter to the Purchaser.

63.	Termination for Convenience

63.1   	The Purchaser, by written notice sent to the Supplier, may terminate the Contract, in whole or in part, at any time for its convenience. The notice of termination will specify the termination is for the Purchaser's convenience, the extent to which performance of the supplier under the Contract is terminated, and date upon which termination becomes effective.

63.2 	However the Materials / equipment that are complete and ready for shipment within thirty (30) days after the supplier's receipt of notice of termination will be accepted by the Purchaser at the Contract terms and prices.

64.	Force Majeure

64.1	The Supplier will not be liable for forfeiture of its performance security, penalty for late delivery, or termination for default if and to the extent that its delay in performance or other failure to perform its obligations under the Contact is the result of an event of Force Majeure.

64.2  	For purposes of this clause, "Force Majeure" means an event beyond the control of the Supplier and not involving the Supplier's fault or negligence and not foreseeable.  Such events may include, but are not restricted to, wars or revolutions fires, floods, epidemics, quarantine restrictions, and freight embargoes.

64.3   	If a Force Majeure situation arises, the supplier will promptly notify the Purchaser in writing of such condition and the cause thereof.  Unless otherwise directed by the Purchaser in writing, the Supplier will continue to perform its obligations under the Contract as far as is reasonably practice, and will seek all reasonable alternative means for performance not prevented by the Force Majeure event.

No price variance will be allowed during the period of force measure.

65.	Settlement of Disputes

65.1	If any dispute or difference of any kind whatsoever will arise between the Purchaser and the Supplier in connection with or arising out of the Contract, the parties will make every effort to resolve amicably such dispute or difference by mutual consultation.

65.2	If, after thirty (30) days the parties have failed to resolve their dispute or difference by such mutual consultation, then either the Purchaser or the Supplier may give notice to the other party of its intention to commence arbitration, as hereinafter provided, as to the matter in dispute, and no arbitration in respect of this matter may be commenced unless such notice is given.

65.3	Any dispute of difference in respect of which a notice of intention to commence arbitration has been given in accordance with this Clause will be finally settled by arbitration.  Arbitration may be commenced prior to or after delivery of the Materials / equipment under the Contract.

65.4	Arbitration proceedings will be conducted in accordance with the following rules of procedure. The dispute resolution mechanism will be as follows:

(a) 	In the case of a dispute or difference arising between the Purchaser and a Supplier relating to any matter arising out of or connected with this agreement, such dispute or difference will be settled in accordance with the Arbitration and Conciliation Act. 1996.  The Arbitral Tribunal will consist of three Arbitrators one each to be appointed by the Purchaser and the supplier the Third Arbitrator will be chosen by the two Arbitrators so appointed by the parties and will acts as Presiding Arbitrator. In case of failure of the two Arbitrators appointed by the parties to reach upon a consensus within period of 30 days from the appointment of the Arbitrator appointed subsequently, the Presiding Arbitrator will be appointed by The Institution of Engineers (India).

- If one of the Parties fails to appoint its Arbitrator in pursuance of Sub-Clause (a) within 30 days after receipt of the notice of the appointment of its Arbitrator by The Institution of Engineers (India), will appoint the Arbitrator.  A certified copy of the order of the Institution of Engineers (India), making such an appointment will be furnished to each to the parties.

- Arbitration Proceedings will be held at Purchaser’s Headquarters, and the language of the Arbitration Proceedings and that of all documents and communication between the parties will be English.

- The decision of the majority of Arbitrators will be final and binding upon both parties.  The cost and expenses of Arbitration Proceedings will be paid as determined by the Arbitral Tribunal.  However, the expenses incurred by each party in connection with the preparation, presentation etc., of its proceedings as also the fees and expenses paid to the Arbitrator appointed by such party or on its behalf will be borne by each party itself.

- Where the value of the Contract is Rs. One Crore and below, the disputes or differences arising will be referred to the Sole Arbitrator.  The Sole Arbitrator should be appointed by agreement between the parties; failing such agreement, by the appointing authority namely The Institution of Engineers (India).

65.5	Notwithstanding any reference to arbitration herein,

- The parties will continue to perform their respective obligations under the Contract unless they otherwise agree; and

- The Purchaser will pay the Supplier any monies due the Supplier.

66.	Jurisdiction

All and any disputes or differences arising out of or touching this contract will be decided by the Courts or Tribunals situated in Purchaser’s Headquarters only. No suit or other legal proceedings will be instituted elsewhere.

67.    	Notices

67.1	Any notice given by one party to the other pursuant to this Contract will be sent to the other party in writing or by cable, telex, or facsimile and confirmed in writing to the other party’s address.

67.2  	A notice will be effective when delivered or on the notice's effective date, whichever is later.

68.	Foreign Exchange

No Foreign Exchange is available or expected for this purchase. Offers which do not require release of F.E. or procurement of import license by TSSPDCL only will be considered. Where some of the components are to be imported the manufacturer will have to make their own arrangements for import license etc., and should not look for any assistance from TSSPDCL.

SECTION-IV

SCHEDULE OF REQUIREMENT

STN-746/21

| Sl. No. | Description | Qty. (Nos.) | Free at Destination Stores |
| --- | --- | --- | --- |
| 1. | Three phase (10-40)A Whole Current Electronic Energy meters of class 1.0 accuracy with IRDA Port with net-metering features housed in PP Box The following cables shall be supplied One in every 20 Nos. Net Meters. - RS 232 (terminated with RJ11) to USB RS 232 (terminated with RJ11) to CMRI | 3,000 | Any district stores In TSSPDCL jurisdiction. |

NOTE:

- In e-procurement commercial stage, if F&I charges are applicable then mention whether F&I  charges entered are exclusive/inclusive of GST in the remarks section. If not mentioned in remarks, F&I charges will be considered as inclusive of GST.

- The tenderer should quote the rates for free at destination stores and shall fill the price schedule in e-procurement platform.

3.	2 Nos. (One) sample of  quoted item shall be submitted at the time of submission of bid. Bids received without samples will be rejected.

The purchaser will not be responsible for any damage that may be caused to the samples at                      	any time

4.	Delivery: To commence in 45 days and complete within 3 (Three) months from the date of receipt of purchase order.

Stores					Circle

Mahaboob Nagar			Mahaboob Nagar

Nalgonda				Nalgonda

Medak 				Sanga Reddy

Siddipet 				Siddipet

Ranga Reddy				Ranga Reddy-South.

City-Hyderabad.			Hyderabad-North.

SECTION-V

QUALIFICATION REQUIREMENTS

SPECIFICATION No. STN-746/21

1.	The bidder must possess BIS and ISO certifications The bidder should be a manufacturer who must have designed, manufactured, tested and supplied to power utilities at least 40% of the quoted quantity of the goods / equipment of same or higher class indicated in the “Schedule of material” in one continuous period of 12 months during the last 5 years and its financial turnover during any one year of the last five years should have been equal or more than 100% value of the material now quoted.

At least 20% of similar material offered against this Specification should be in successful operation since 2 years as on the date of opening of the Bid with documentary evidence.

( Performance Certificates issued by head of purchase wing will only be considered)

Fresh bidders can be given order upto 15% of total quantity as a trial order if equipment is justified.

Any company/vendor/supplier/contractor that is blacklisted/debarred by any other power utility is not eligible to participate in the tenders.

The bidders shall have to furnish an undertaking in the prescribed format (at page               no.68) regarding any relation to the promoters of blacklisted / debarred companies by any utility. Any false information furnished in the declaration while rendering bid, such contract is liable for termination as well as recovery of damages.

2.	The bidder should furnish the information on all past supplies and satisfactory performance in proforma under Form 6 attested by a CA.

3.	All bids submitted will also include the following information:

i.	Copies of original documents defining the constitution or legal status, place of registration and principle place of business of the company or firm or partnership, etc.,

ii.	The bidder should furnish a brief write-up, backed with adequate data, explaining his available capacity and experience (both technical and commercial) for the manufacture and supply of the required equipment within the specified time of completion after meeting all their current commitments.

iii.	The bidder should clearly confirm that all the facilities exist in his factory for inspection and testing and these will be made available to the purchaser or his representative for inspection.

iv.	Reports on financial standing of the Bidder such as profit and loss statement, balance sheets and auditor’s report for the past five years, bankers certificates etc.

4.	The bidder shall furnish Type Test Reports. The type tests must have been conducted on the material offered as per the relevant IS/CBIP in recognized NABL laboratory as per the latest revision of the Technical Specification and the date of Type tests will not be later than                     3 years.  The Bids received without type test reports will be treated as Non-Responsive.

5.	Even though the bidder meets the above qualifying criteria, they are subject to be disqualified if they have…

a.	made misleading or false representations in the forms statements and attachments submitted in proof of qualification requirements and / or

b.	record of poor performance such as not properly completing the contract, inordinate delays in supply completion, litigation history or financial failure etc.

### 6.	Not withstanding anything stated above the purchaser reserves the right to assess bidder’s 	capability and capacity to perform the contract should circumstances warrant such an 	assessment in the overall interest of the purchaser.

### 7.	Two (2) Nos. samples of Three phase, Electronic meter with net-metering features in PP Box (class 1.0 accuracy) programmed as under shall accompany the tender.  Tenders received without samples are liable for rejection.

Voltage    -	240V phase to neutral.

Current    -	10-40 A

SECTION-V

TECHNICAL SPECIFICATION STN-746/21

Three phase, Electronic meter with net-metering features in PP Box (class 1.0 accuracy)

1.0     SCOPE :

1.1	This specification covers design, engineering, manufacture, assembly, stage testing, inspection and testing before supply and delivery  at destination stores of 3 phase 4 wire direct connected static Trivector Energy Meters (10-40A) with IrDA communication bi-directional energy meter ( solar net meters)  as per requirement given in this specification in pilfer proof box.  The meter shall be suitable for measurement of energy and power, demand  requirement in an AC balanced / unbalanced system over a power factor  range of zero  to unity (Lag / Lead).  These meters should have another communication port (RJ11) to interface for remote meter reading/Offline data downloading and shall also have  IrDA port for spot billing through ISBM.

The manufacturer shall differentiate the import & export energy clearly ( by inward / outward arrow marking etc.) Energy supplied to the consumer  is import energy & Energy received from the consumer is export energy.

The above meters shall be supplied in a pilfer proof box which shall be weather proof made out of transparent Polycarbonate with flame retardant properties.  The meter and box should be supplied in suitable packing so as to withstand transit shocks.

  - It is not the intent to specify completely herein all the details of the design and construction of material.  However the material shall conform in all respects to high standards of engineering, design and workmanship and shall be capable of performing in continuous commercial operation, in a manner acceptable to the purchaser, who will interpret the meanings of drawings and specification and shall have the power to reject any work or material which, in his judgment is not in accordance therewith.  The offered material shall be complete with all components necessary for their effective and trouble free operation.  Such, components shall be deemed to be within the scope of Bidder's supply irrespective of whether those are specifically brought out in this specification and/or the commercial order or not.

  - The original manufacturers of LT A.C. Static Three Phase energy meters shall only quote against this tender. In case of foreign manufactures their authorized agent may also bid provided that they should be registered vendor and shall have all the testing facilities in India. They should also produce the documents authorizing them as agents, in India.

  - It is mandatory that in case of all manufacturers, the offered meter shall be ISI marked and bidder shall have to furnish valid BIS certificate along with the offer.

2.0.	STANDARDS:

2.1  Unless specified elsewhere in this specification, the performance & 	testing of the  meters should conform to the following Indian / International standards, to be read with  up to-date and latest 	amendments / revisions thereof as on 90 days prior to floating of 	tender.

- Indian Standard No. IS 13779 of 1999 with latest amendments - AC         	  Static Watt hour Meters, Class 1 – Specification.

- IEC 61358:1996-Acceptance inspection for direct connected 	meters.

- IEC 62052&53-Particular requirements for direct connected 	meters.

- IEC 61000-4-5:2001-04-immunity tests.

- IS.14697 of 1999 – Clause 1.3.(for APF)

- IS.12063 – Degree of protection for enclosures.

- IS.12346 –Testing equipments.

- IEC 62053-11, 21&61-test, requirement & power consumption.

- IEC-61000-4, 5 & 6- EMI/EMC Withstand

- IS 11000-   Fire hazard testing

- IS-9000 – BET procedures.

- IEC.15707, 2006- Testing & maintenance of AC meters, code of 	practice.

(14) CBIP-304/July 2008-Standardization of AC Static Electrical 	Energy Meters.

(15)    CEA installation and operation of meters regulations with all   amendments.

2.2	CONFLICT OF STANDARDS :

Material conforming to other internationally accepted standards, which ensure equal or higher quality than the standards mentioned above would also be acceptable. In case the Bidders who wish to offer material conforming to the other standards, salient points of difference between the standards adopted and the specific standards shall be clearly brought out in relevant schedule. Two copies of such standards with authentic English Translations, shall be furnished along with the offer. In case of conflict the order of precedence shall be (i) IS (ii) CBIP 325 and (iii) other standards.  In case of any difference between provisions of these standards and provisions of the specification, the provisions contained in specification shall prevail.

3.0	CLIMATIC CONDITIONS :

The materials to be supplied against this specification shall be suitable for satisfactory continuous operation under the following tropical conditions.

| # Location | At various locations in the state of Andhra Pradesh |
| --- | --- |
| Max. ambient air temperature (deg.C) | 50 |
| Max. ambient air temperature in a closed box (deg.C) | 60 |
| Min. ambient air temperature (deg.C) | 7.5 |
| Average daily ambient air temp. (deg.C) | 35 |
| Max. Relative Humidity (%) | 100 |
| Max. altitude above mean sea level (m) | 1000 |
| Average Annual rainfall(mm) | 925 |
| Max. wind pressure(kg/sq. m.) | 200 |
| Isoceraunic level(days per year) | 50 |
| Seismic level(Horizontal acceleration) | 0.3 g. |
| Permitted Noise Level | 45 dB |

Moderately hot and humid tropical climate is conducive to rust and fungus growth.  The climatic conditions are also prone to wide variations in the ambient conditions, Smoke is also present in the atmosphere, Heavy lightning also occurs during June to October.

4.0.	PRINCIPAL PARAMETERS :

The equipment shall conform to the following specific parameters:

| Sl. No. | Item | Specification |
| --- | --- | --- |
| 1. | Type of Installation | Indoor |
| 2. | System voltage | 3x240V +20%, -40% Phase to neutral |
| 3. | System frequency | 50 Hz +/- 5% |
| 4. | No. of phases | Three Phase 4wire |
| 5. | System of earthing | Solidly grounded |
| 6. | Current rating | 0.2% of Imin of 10-40A to 150% of I max for 10-40A |
| 7. | Power factor range | Zero lag – Unity – Zero lead |
| 8. | Resistance to impulse voltage | Minimum 10KV peak as per IS test procedure. |
| 9. | Resistance to surge voltage | Minimum 8KV peak of 1.2/50 Micro sec. |
| 10. | Test Voltage at 50 Hz for 1min | 4 KV rms – as per IS 13779 |
| 11. | Clock time accuracy | +/- 5 min/year – as per CBIP - 325 |

4.1.	The limits of error for +20 to -40% Vref variations shall be as under:-

(a) @ UPF 0.7% for Ib, (b) @ 0.5 lag 1.0% for Ib, (c) @ UPF 0.6% for 0.6 Ib & Imax with 10% 0f 3rd harmonic current in circuit.

5.0.  	TECHNICAL REQUIREMENTS:

    - Ratings :

- Three phase meters as specified at clause 1.0 shall be rated as follows:

| a) | Voltage | 3 x 240V (Phase to neutral) |
| --- | --- | --- |
| b) | Current |  |
|  | i) Basic current (Ib) | 10A |
|  | ii) Rated Max. Current (Imax) | 40A |
| c) | Frequency | 50 Hz |
| d) | Accuracy | Class 1.0 |

5.1.3	Power Supply Variation:

The extreme power supply variation which the meter should withstand without damage and without degradation of its metrological characteristics when it is subsequently operated under its normal operating conditions:

| Voltage | -40% to +20% |
| --- | --- |
| Frequency | +/- 5% |
| PF.range | Zero lag-unity-zero lead (*) |

(*)  	The meter shall work over wide PF range and the limits of errors with the variation of PF shall be as per IS 13779 (latest version).

However manufacturer can offer meters which can withstand higher variations of voltage and frequency.

Note :	The meter shall remain powered up and functional even in the event of only one phase  is available.

The meter shall be able to continuously withstand phase to phase voltage of 500V

Name Plate marking : The name plate drawing shall be got approved from the purchaser before commencement of manufacture.

    - Accuracy:  Class of accuracy of meter shall be 1.0. The accuracy should not drift with time. The reactive accuracy class of the meter shall be same as the active accuracy class.  The internal least count of energy recording shall not be more than 0.01 KWH/KVAH hence every 0.01 Kwh/Kvah consumption will be internally stored. Also there shall be no loss of energy registration on account of power outages due to high start up time of the meter. To verify, the above the meter will be switched off/on 40 times at rated parameters and energy recording on display with decimal digit should be within 0.4 Kwh/Kvah of the energy, it should register, as per its accuracy at that load. This will be verified during testing sample meters and at works during inspection. The meter reading should not be disturbed during sudden switching of heavy loads or transient voltage spikes.

    - CTs/SHUNT ARRANGEMENT

The meter shall operate on CT or shunt. The current circuit shall be appropriately insulated and designed to withstand the temperature rise of 50˚C over the ambient at maximum current. Specific confirmation to be submitted by the vendor that the accuracy of measurement will not suffer due to utilization of shunt on account of thermal variation and temperature coefficient up to an operational temperature of 80˚C  and shall comply with IS:13379(cl.9.4).The CTs shall have proper magnetic shield and shall be mounted firmly without any movement. The bidders shall submit the details of the shunt and how they are protected against external influences & temperature variations.

  - Power consumption:

5.2.1 	Voltage circuit:  The active and apparent power consumption in each voltage circuit including power supply of meter at reference voltage, reference temperature and reference frequency shall not exceed 1 Watt and 4 VA per phase respectively.

5.2.2 	Current circuit:  The apparent power taken by each current circuit at basic current, reference frequency and reference temperature shall not exceed 1VA.

The above losses are maximum allowable and there would not be any positive tolerance.

5.2.3	Starting current:  The meter should start registering energy at 0.2% of basic current.

5.2.4	Running with no load: When the voltage of 120% of rated voltage is applied with no current flowing in the circuit, the test output of the meter shall not produce more than one pulse/count. The minimum time test limit shall be as per IS 13779/1999.

  - Influence quantity: As per  CBIP -325 .

  - Super capacitor

The meter shall have a super capacitor with sufficient capacity to enable the meter reader to take reading under power off condition with following provisions:

Suitable rechargeable super capacitor back up for continuous display for 48 hours from instant of power failure. The display should be powered up through push button only when power failure occurs. This arrangement shall be robust such that down loading of meter data during power off condition is not affected and minimum three down loads are guaranteed for a outage. There shall be a suitable backup provision for display in case of super capacitor failure. The performance of the super capacitor shall be verified by removing all the batteries from the circuit in any meter during sample   testing or inspection. The charging time of super capacitor shall not be more than 6 hours.

In any case, RTC battery power shall not be used for display under power off condition. Battery used for the meter display during power off condition shall be separate from the battery used for the real time clock.

5.4.1  Real time clock and battery:

- The MD integration cycle shall be on the function of RTC of the meter. The maximum drift in real time clock of the meter shall not exceed plus or minus 5 minutes per year as per CBIP 325and crystal should be temperature compensated for temperature range of 0 to 50˚C when powered by internal battery or supply. This shall be verified during sample testing and inspection. A non-chargeable lithium battery of adequate storage energy with 10 year guarantee period only should be provided. Necessary document to this effect has to be submitted along with the tender. If the battery fails within meter warranty period the meter should be replaced by the supplier within 15 days from the date of intimation failing which the entire cost of the meter will be recovered from the balance payment due to the supplier.

- The Synchronization of Meter RTC Time/day shall be possible through password / key code enabled command from the Remote Server. In case of meter connected to AMR system through GSM/GPRS/PLCC modem, the meter should be able to synchronize its clock with the system time. Super capacitor used for the meter display during power off condition shall be separate from the battery used for the real time clock.

- Facility for correcting the drift in Real Time clock through CMRI has to be provided with proper security. Whenever RTC is corrected, all the registers and other parameters shall be updated. The date and time should be user programmable. The meter should be capable of storing in the memory the readings of a specified date and time in a month / two months for the purpose of retrieving the same at a later date without change in the specified timing while correcting the drift.

- The data stored in the memory shall not be lost or updated when the meter is in power off condition, so that same are retrievable even after lapse of several months. (This is to enable utility to defend their cases legally in case of disputed meters/billing revision.)

5.4.2  Non volatile Memory:

The meter should have non volatile memory, so that the registered parameters will not be affected by loss of power.  The non volatile memory should have a minimum retention time of 10 years. It is the responsibility of the meter manufacturer to retrieve the data from this memory, in the event of display failure and other defects except for completely burnt meter as and when requested by the purchaser with in a period of 30 days from the date of intimation. The transportation cost for the same should be borne by the supplier. If the data could not be retrieved for any reasons the same shall be communicated to the respective circle M&P/MRT with the reason for non retrieval.

6.0	Measuring parameters:

The three phase meter shall be capable to measure continuously “KWh/KVarh/KVah” at all loads and power factors i.e., zero lag-unity-zero lead under balanced and unbalanced conditions of load for both Import & Export.  The meter should also have provision for automatic recording of cumulative kwh/Kvah at 24.00 Hrs. on the last day of the month for each calendar month and the same should go to memory.  In addition it shall measure and display in auto scroll mode, through a manual switch (push button) and also to read with CMRI/remote read out the following :

6.1      Parameters (Auto Scroll)

| 1 | LCD Segment Display |
| --- | --- |
| 2 | Meter Serial Number |
| 3 | Date |
| 4 | Time |
| 5 | Cumulative Total Active import energy |
| 6 | Cumulative Total Active export energy |
| 7 | Cumulative Reactive import lag |
| 8 | Cumulative Reactive export lag |
| 9 | Cumulative Reactive import lead |
| 10 | Cumulative Reactive export lead |
| 11 | Cumulative Total Apparant import energy |
| 12 | Cumulative Total Apparant export energy |
| 13 | Cumulative Net Active energy (import-export) |
| 14 | Signed Instantaneous PF |
| 15 | TOD (0-24 Hrs) Apparent Import MD |
| 16 | TOD (0-24 Hrs) Apparent Import MD with Date and Time |
| 17 | TOD (0-24 Hrs) Active Import MD |
| 18 | TOD (0-24 Hrs) Active Import MD with Date and Time |
| 19 | TOD (0-24 Hrs) Apparent Export MD |
| 20 | TOD (0-24 Hrs) Apparent Export MD with Date and Time |
| 21 | TOD (0-24 Hrs) Active Export MD |
| 22 | TOD (0-24 Hrs) Active Export MD with Date and Time |
| 23 | Cumulative Tamper Count |

6.2      Display Parameters (Push Button) :

The display of following parameters   shall be continuously scrolling one after another through push button. The display shall have `ON’ time of 10 seconds for each measured value for display cycling.

| 1 | LCD Segment Display |  |
| --- | --- | --- |
| 2 | Meter Serial Number |  |
| 3 | Date |  |
| 4 | Time |  |
| 5 | Cumulative Total Active import energy |  |
| 6 | Cumulative Total Active export energy |  |
| 7 | Cumulative Net Active energy (import-export) |  |
| 8 | Cumulative Reactive import lag |  |
| 9 | Cumulative Reactive export lag |  |
| 10 | Cumulative Reactive import lead |  |
| 11 | Cumulative Reactive export lead |  |
| 12 | Cumulative Total Apparant import energy |  |
| 13 | Cumulative Total Apparant export energy |  |
| 14 | Signed Instantaneous PF |  |
| 15 | TOD (0-24 Hrs) Apparent Import MD |  |
| 16 | TOD (0-24 Hrs) Apparent Import MD with Date and Time |  |
| 17 | TOD (0-24 Hrs) Active Import MD |  |
| 18 | TOD (0-24 Hrs) Active Import MD with Date and Time |  |
| 19 | TOD (0-24 Hrs) Apparent Export MD |  |
| 20 | TOD (0-24 Hrs) Apparent Export MD with Date and Time |  |
| 21 | TOD (0-24 Hrs) Active Export MD |  |
| 22 | TOD (0-24 Hrs) Active Export MD with Date and Time |  |
| 23 | Cumulative Tamper Count |  |
| 24 | Battery Status |  |
| 25 | R-Ph Current |  |
| 26 | Y-Ph Current |  |
| 27 | B-Ph Current |  |
| 28 | R-Ph. Voltage |  |
| 29 | Y-Ph. Voltage |  |
| 30 | B-Ph. Voltage |  |
| 31 | Inst Signed R-Ph PF |  |
| 32 | Inst Signed Y-Ph PF |  |
| 33 | Inst Signed B-Ph PF |  |
| 34 | Supply Frequency |  |
| 35 | Present Voltage and Current Status AND Phase Sequence (Voltage) AND Current Sequence |  |
| 36 | Inst Signed Active Load |  |
| 37 | Inst Signed Reactive Load |  |
| 38 | Inst Signed Apparent Load |  |
| 39 | Instantaneous Average PF |  |
| 40 | MD Reset Count |  |
| 41 | Cumulative Apparent MD Import |  |
| 42 | Cumulative Apparent MD Export |  |
| 43 | Cumulative Active MD Import |  |
| 44 | Cumulative Active MD Export |  |
| 45 | H1 Cumulative Active Energy Import |  |
| 46 | H2 Cumulative Active Energy Import |  |
| 47 | H3 Cumulative Active Energy Import |  |
| 48 | H4 Cumulative Active Energy Import |  |
| 49 | H5 Cumulative Active Energy Import |  |
| 50 | H6 Cumulative Active Energy Import |  |
| 51 | H1 Cumulative Active Energy export |  |
| 52 | H2 Cumulative Active Energy export |  |
| 53 | H3 Cumulative Active Energy export |  |
| 54 | H4 Cumulative Active Energy export |  |
| 55 | H5 Cumulative Active Energy export |  |
| 56 | H6 Cumulative Active Energy export |  |
| 57 | H1 Cumulative Reactive Lag Energy import |  |
| 58 | H2 Cumulative Reactive Lag Energy import |  |
| 59 | H3 Cumulative Reactive Lag Energy import |  |
| 60 | H4 Cumulative Reactive Lag Energy import |  |
| 61 | H5 Cumulative Reactive Lag Energy import |  |
| 62 | H6 Cumulative Reactive Lag Energy import |  |
| 63 | H1 Cumulative Reactive Lag Energy export |  |
| 64 | H2 Cumulative Reactive Lag Energy export |  |
| 65 | H3 Cumulative Reactive Lag Energy export |  |
| 66 | H4 Cumulative Reactive Lag Energy export |  |
| 67 | H5 Cumulative Reactive Lag Energy export |  |
| 68 | H6 Cumulative Reactive Lag Energy export |  |
| 69 | H1 Cumulative Reactive Lead Energy import |  |
| 70 | H2 Cumulative Reactive Lead Energy import |  |
| 71 | H3 Cumulative Reactive Lead Energy import |  |
| 72 | H4 Cumulative Reactive Lead Energy import |  |
| 73 | H5 Cumulative Reactive Lead Energy import |  |
| 74 | H6 Cumulative Reactive Lead Energy import |  |
| 75 | H1 Cumulative Reactive Lead Energy export |  |
| 76 | H2 Cumulative Reactive Lead Energy export |  |
| 77 | H3 Cumulative Reactive Lead Energy export |  |
| 78 | H4 Cumulative Reactive Lead Energy export |  |
| 79 | H5 Cumulative Reactive Lead Energy export |  |
| 80 | H6 Cumulative Reactive Lead Energy export |  |
| 81 | H1 Cumulative Apparent Import Energy |  |
| 82 | H2 Cumulative Apparent Import Energy |  |
| 83 | H3 Cumulative Apparent Import Energy |  |
| 84 | H4 Cumulative Apparent Import Energy |  |
| 85 | H5 Cumulative Apparent Import Energy |  |
| 86 | H6 Cumulative Apparent Import Energy |  |
| 87 | H1 Cumulative Apparent export Energy |  |
| 88 | H2 Cumulative Apparent export Energy |  |
| 89 | H3 Cumulative Apparent export Energy |  |
| 90 | H4 Cumulative Apparent export Energy |  |
| 91 | H5 Cumulative Apparent export Energy |  |
| 92 | H6 Cumulative Apparent export Energy |  |
| 93 | H1 MD in KW Import |  |
| 94 | H2 MD in KW Import |  |
| 95 | H3 MD in KW Import |  |
| 96 | H4 MD in KW Import |  |
| 97 | H5 MD in KW Import |  |
| 98 | H6 MD in KW Import |  |
| 99 | H1 MD in KW export |  |
| 100 | H2 MD in KW export |  |
| 101 | H3 MD in KW export |  |
| 102 | H4 MD in KW export |  |
| 103 | H5 MD in KW export |  |
| 104 | H6 MD in KW export |  |
| 105 | H1 MD in KVA Import |  |
| 106 | H2 MD in KVA Import |  |
| 107 | H3 MD in KVA Import |  |
| 108 | H4 MD in KVA Import |  |
| 109 | H5 MD in KVA Import |  |
| 110 | H6 MD in KVA Import |  |
| 111 | H1 MD in KVA export |  |
| 112 | H2 MD in KVA export |  |
| 113 | H3 MD in KVA export |  |
| 114 | H4 MD in KVA export |  |
| 115 | H5 MD in KVA export |  |
| 116 | H6 MD in KVA export |  |
| 117 | H1 Avg PF |  |
| 118 | H2 Avg PF |  |
| 119 | H3 Avg PF |  |
| 120 | H4 Avg PF |  |
| 121 | H5 Avg PF |  |
| 122 | H6 Avg PF |  |
| 123 | Last Cover open time |  |
| 124 | Last Cover open date |  |
| 125 | R-Ph. Voltage THD |  |
| 126 | Y-Ph. Voltage THD |  |
| 127 | B-Ph. Voltage THD |  |
| 128 | R-Ph. Current THD |  |
| 129 | Y-Ph. Current THD |  |
| 130 | B-Ph. Current THD |  |
| 131 | Present CT Status |  |
| 132 | Present PT Status |  |
| 133 | Present Others Status |  |
| 134 | Cumulative Present CT Status |  |
| 135 | Cumulative Present PT Status |  |
| 136 | Cumulative Present Others Status |  |
| 137 | First Occurrence Tamper ID |  |
| 138 | Time of 1st Tamper Occurrence |  |
| 139 | Date of 1st Tamper Occurrence |  |
| 140 | Last Occurrence Tamper ID |  |
| 141 | Time of Last Tamper Occurrence |  |
| 142 | Date of Last Tamper Occurrence |  |
| 143 | Last Restoration Tamper ID |  |
| 144 | Time of Last Tamper Restoration |  |
| 145 | Date of Last Tamper Restoration |  |
| 146 | R Phase CT Reversal Count |  |
| 147 | Y Phase CT Reversal Count |  |
| 148 | B Phase CT Reversal Count |  |
| 149 | CT Bypass Count |  |
| 150 | Current Imbalance Count |  |
| 151 | Over Current Count |  |
| 152 | R Phase PT Miss Count |  |
| 153 | Y Phase PT Miss Count |  |
| 154 | B Phase PT Miss Count |  |
| 155 | Voltage Unbalance Count |  |
| 156 | Invalid Voltage Count |  |
| 157 | Neutral Distrubance Count |  |
| 158 | Low Power Factor Count |  |
| 159 | R Phase Miss Current Count |  |
| 160 | Y Phase Miss Current Count |  |
| 161 | B Phase Miss Current Count |  |
| 162 | R Phase CT Open Count |  |
| 163 | Y Phase CT Open Count |  |
| 164 | B Phase CT Open Count |  |
| 165 | High Voltage Count |  |
| 166 | Low Voltage Count |  |
| 167 | Version |  |
| 168 | Self Diagnostic Features |  |

|  | HR MODE |
| --- | --- |
| 1 | HR Cumulative Active Import Energy |
| 2 | HR Cumulative Reactive Import Lag Energy |
| 3 | HR Cumulative Reactve Import Lead Energy |
| 4 | HR Cumulative Apparent Import Energy |
| 5 | HR Cumulative Active export Energy |
| 6 | HR Cumulative Reactive export Lag Energy |
| 7 | HR Cumulative Reactve export Lead Energy |
| 8 | HR Cumulative Apparent export Energy |
| 9 | Raising MD in KW Import |
| 10 | Raising MD in KW Export |
| 11 | Raising MD in KVA Import |
| 12 | Raisiing MD in KVA Export |

|  | BATTERY MODE |
| --- | --- |
| 1 | LCD Segment Display |
| 2 | Meter Serial Number |
| 3 | Date |
| 4 | Time |
| 5 | Cumulative Total Active import energy |
| 6 | Cumulative Total Active export energy |
| 7 | Cumulative Reactive import lag |
| 8 | Cumulative Reactive export lag |
| 9 | Cumulative Reactive import lead |
| 10 | Cumulative Reactive export lead |
| 11 | Cumulative Total Apparant import energy |
| 12 | Cumulative Total Apparant export energy |
| 13 | Cumulative Net Active energy (import-export) |
| 14 | Signed Instantaneous PF |
| 15 | TOD (0-24 Hrs) Apparent Import MD |
| 16 | TOD (0-24 Hrs) Apparent Import MD with Date and Time |
| 17 | TOD (0-24 Hrs) Active Import MD |
| 18 | TOD (0-24 Hrs) Active Import MD with Date and Time |
| 19 | TOD (0-24 Hrs) Apparent Export MD |
| 20 | TOD (0-24 Hrs) Apparent Export MD with Date and Time |
| 21 | TOD (0-24 Hrs) Active Export MD |
| 22 | TOD (0-24 Hrs) Active Export MD with Date and Time |
| 23 | Cumulative Tamper Count |

6.3. 	Readout Parameters with CMRI/RMR/IRDA. :

- Meter serial number, Model, Make.

- All parameters at Clause 6.1 & 6.2. (Above).

- Load Survey data.

- Tamper details of at least 200 events (in and out) with date and time

- Self diagnostic details (Real time calendar, low battery).

- The meter should have visual quadrant representation on the LCD for energy measurement.  Relevant  quadrant in which metering is taking place should be in on state for ease of understanding.

Note : Meter shall continuously monitor and calculate the average 	maximum demand 	for each demand interval time of 30 minutes 	and maximum of these in a calendar 	month shall be stored 	along with date and time when it occurred.  Whenever MD 	is reset, the maximum MD value so registered shall be stored along with 	date 	and time.

- Meter should be suitable for lag only tariff, blocking the leading PF, satisfying the formula KVAH2 = KWH2 + RKVAH2 for lagging loads, KVAH2 = KWH2 for leading loads.

- The meter should measure the total energy consisting of 50 Hz energy and harmonic energy both for active as well for reactive. Provision for displaying the THD in % for voltage and current in each phase (Minimum up to 21st order) shall be made available in the push button mode.

- The Average power factor for the billing period may be calculated as per IS.14697 of 1999 – Clause 1.3.and G-7.

6.4 	In addition to providing on the Name plate, the meter serial number shall also be programmed into meter memory for identification through CMRI/remote reading and meter reading print out.

The bidder shall indicate any additional measurement and display features being offered in addition to the above minimum requirement.

6.5   MD Reset :  The meter should have provision of maximum demand resetting : (i) Manual resetting (ii) Resetting shall be possible through a  handheld Common Meter Reading Instrument (CMRI)  capable of communicating with the meter with the help of Lap Top. (iii) Auto reset at 24.00 Hrs of the last date of each calendar month for which minimum 30 years calendar shall be programmed by the manufacturer. The cumulative KWh&Kvah (Imp and Export)	should also be recorded at 24.00 Hrs. on the last date of each calendar month for previous six months. DIP shall be set at 30 minutes duration.  DIP shall commence at the fixed time intervals of real time.

MD recording of Block method is to be used.  Necessary software is to 	be provided 	for changing DIP to 15minutes.

The rising value of current demand with rising time should be held in the memory in the event of interruption (or) switching off power supply and it should not fall to zero on such instances.

The meter shall have the following MD resetting options.

- Automatic reset at the at 24.00 hrs. of last  day of the calendar month.

- Manual resetting arrangement (MD reset button) with sealing facility.

- MD reset through authenticated transaction.

7.0    LCD Display:

The meters shall have bright LCD Electronic display with backlit and with minimum (6+1) digits. The backlit should not glow during power off condition. The LCD shall be industrial grade with multi layer & of STN (Super Twisted Nematic) type construction suitable for temperature withstand of 80°c (storage) & 65°c (operation) i.e.,

- When the meter is placed over at a constant temperature of 65°c for a period of 30 minutes, the character of LCD should not deform.

- After keeping the meter at a constant temperature of 80°c for a period of 30minutes and when restores at normal temperature, LCD display shall work satisfactorily.

Note: The LCD should be hard pin type and soldered to PCB.

The LCD display should have a wide viewing angle of 120° and up to one meter distance, for clear visibility of the display of the meter reading at distance with backlight in green and characters/digits in black. Large viewing area with large display icons is preferred.  However, the display size area should not be less than 55 x 14 mm. The registered parameters shall not be affected by loss of power. The display shall not be affected by electrical and magnetic disturbances. The data should be stored in non-volatile memory. The non-volatile memory should retain data for a period of not less than 10 years under unpowered condition. Battery back-up memory will not be considered as NVM.

The register shall be able to record and display starting from zero, for a minimum of 2500 hours. The energy corresponding to rated maximum current at reference voltage and unity power factor. The register should not roll over in between this duration. In addition to provide Serial Number of the meter on the display plate, the meter serial should also be programmed into meter memory for identification through communication port for CMRI / laptop / meter reading printout.

The minimum character height x width shall be 10x5mm. Dot matrix type LCD display is not acceptable.

All important data such as calibration data, billing parameters and cumulative KWh/KVAh should be stored in Non-Volatile Memory (NVM) internal to the main processing circuit and it should not be possible to change the data through any standard serial communication.

The accuracy of display parameters on LCD display for all parameters shall be matching with the accuracy class of meters as per IS.

The availability of phase wise voltages and current shall be indicated individually   by the characters 1,2&3 (1,2,3 indicating the availability of R, Y &B phase voltages respectively the availability of corresponding current be indicated by blinking of the corresponding numeric number (phase). At the start of each sequence of display LCD healthiness anomaly and real time and date shall be displayed.

8.0	Test output : The meters shall have a separate pulse emitter and  high resolution display for testing  purpose as described in CBIP Report No.304.

The resolution of the test output shall be sufficient, to enable the conduction of the starting current test in less than 10 minutes and accuracy test at the lowest load shall be completed with desired accuracy within 5 minutes (as per CBIP -304).

9.0	Load Survey Capability :

The meter should log 30 minutes kWh, Kvarh lag, Kvarh lead, Kvah, Kva, pf, three voltages(R,Y,B) and three currents(R,Y,B) for the last 60 days for both import & export.  It should be possible to transfer this data on to a base Computer station/Laptop (of the Purchaser) through CMRI/RMR/P&T lines  as detailed in Cl 6.2  The base computer shall give complete details of load survey particulars both in numeric data form and in graphic form for both import & export directions.  Necessary software for invoking the base computer station shall be provided by the bidder and demonstrated.

a. Cumulative KWH at 00.00 hrs on daily basis (import & export).

b. Cumulative KVAH at 00.00 hrs on daily basis (import & export).

c. Daily Phase-wise VI profile for each 30 minutes with high/low of the day (import & export).

d. Daily demand for each 30 minutes with max/min of the day(import & export).

e. No supply period and no load period on daily basis in hrs&minutes (import & export).

f.THD for voltage and current

- The load survey data, billing parameters and tamper data shall not be updated when the meter is in power off condition. Whenever the meter is released from service condition either for safe custody or due to billing dispute ,the above said data  shall be retained for the period of actual use of meter and shall retrievable as when required. The meter shall have AMR interface facility for Remote Meter Reading through various communication means like PSTN/OPTICAL FIBRE/ GSM/ GPRS/ CDMA/ PLCC/RF coupled with appropriate modem based on communication backbone chosen.  The communication port shall also have a separate sealing provision.

- In the load survey graph, no supply period, no load period is to be distinguished with cumulative values for each day for the above events.

- The RS-232 with RJ11 port provided in the Meter shall be accessible using a USB to Serial converter in case if PC/Laptop communicating to Meter is having only USB Ports instead of RS-232 Ports. The Meter Manufacturer shall also provide one no. compatible USB to RS-232 converter  for each lot of 500 nos. Meters along with RJ11 Interface cables.

- It shall be responsibility of the meter manufacturer to provide required software and all the facilities free of cost to enable the use of IRDA as well as RS232 port for reading and retrieving the data from the meter through CMRI and AMR and to download the data to PC Necessary upgrades of software shall be supplied free of cost for downloading simultaneously the existing parameters and any parameters added in future specifications of meters.

- The solar hours (6AM to 6PM) and non solar hours (6PM to 6AM) energies (kwh, KVah) in import and export shall also be made available in daily midnight snapshots.

10.0	Communication capability :

10.1	The meter should have a properly secured IRDA port in front of the meter for data transfer without error by CMRI/ISBM/HHM and necessary protocol shall be provided by the bidder  compatible to the  existing ISBMs being utilized for billing by utility.

10.2	The meter shall also be provided with a RS-232 communication port ( can also be provided in the form of RJ 11 port) to interface external modem for remote data collection.  RS 232 ( RJ 11) port shall be located under the terminal cover for data transfer or subsequently hooked to remote metering device i.e. to enable for future adoption to any mode of technology for Remote Meter Reading through various  communication means like PSTN/GSM/ GPRS/ CDMA/ PLCC/RF coupled with appropriate modem based on communication backbone chosen.  The communication port shall also have a separate sealing provision if the same was not provided inside the terminal cover.  It has to be designed as read and write, and locking should be provided for writing mode.

10.3	The RS-232/RJ11 port provided in the Meter shall be accessible using a USB to Serial converter in case if PC/Laptop communicating to Meter is having only USB Ports instead of RS-232 Ports. The Meter Manufacturer shall also provide one no. compatible USB to RS-232 converter cable for each lot of 500 nos. Meters.

  - The protocol used in the meter shall have to be provided at the time of supply for the purpose of AMR System. Past suppliers shall have to submit a written undertaking that they will provide protocol for meters supplied so far, the said undertaking shall be submitted along with offer failing which, the offer will be rejected. They will also ensure that protocol for the type of meters supplied in the past will be provided as & when supplies are affected.

  - It shall be responsibility of the meter manufacturer to provide required software and all the facilities free of cost to enable the use of RS 232 port for reading and retrieving the data from the meter through CMRI and AMR and to download the data to PC Necessary upgrades of software shall be supplied free of cost for downloading simultaneously the existing parameters and any parameters added in future specifications of meters..

  - All important data such as billing tamper and load survey should be stored in NVM and same should not be possible to change/tamper these data through any standard serial communication. This will be verified by removing the NVM of the meter and check the working of the meter during sample testing or inspection.

11.0	SOFTWARE:

11.1	Meters manufacturer shall provide the BCS software which should be compatible with latest version of Windows platform and suitable software compatible to CMRI for reading the data from the meters.

  - The computer software shall be user friendly. The data transfer shall be highly reliable and fraud proof (No editing shall be possible on base computer by any means).The software shall have capability to convert all the data into ASCII format All the options available in BCS are to be displayed in the window screen.

11.3	The software to be installed in the CMRI/PC/ Laptop for the purpose of reading   and programming the specific make(s) of static meters shall be made available by each meter manufacturer whose meters are to interface with CMRI/PC.

11.4.	The Software should have polling feature with optional selection of parameters to be downloaded for AMR applications. The Software should have programmable facility to restrict the access to the information recorded at different security levels.

11.5.	If the software supplied is of latest version than the earlier one supplied, then the same shall be such that it is compatible for the meters already supplied and also the meter data already read and available at BCS to the extent possible. Confirmation to this effect shall be furnished along with the offer.

12.0.	The CMRI software should have the following provisions

a.	Collection of data (All Data including dumped)

b.	Download to BCS using same menu in BCS and CMRI

c.	Billing

d.	Load Survey

e.	Tamper

f. 	Setting

g.	Name plate (Meter Sr.No, Meter type, Rating, Meter constant. Integration Period and Guarantee period)

h.	Upload from BCS

i.	Clear CMRI (through CMRI & BCS)

j.	Instant parameters

k.	Accuracy Test (Kwh, Kvah )

l.	Memory Check (to view the no of meters read & balance space available in terms of Number of meters)

13.0	Programming parameters (through CMRI)

  - Demand Integration period

  - MD type (KW and  KVA)

  - Lead Kvarh (lock and unlock)

  - MD Reset

e.	TOD PROGRAMMING

f.	Real Time Clock, Date & Time

g.	Profile Capture period (24hrs-minimum, 90days-maximum)

h.	Auto Reset date and time every month.

13.1.	The meter reading software should be capable of transferring data including load survey & the entire meter data from meter to CMRI within 5 minutes shortest time. The time taken to complete the process of data collection from the meter thro CMRI and upload to BCS should be within 5 minutes. The data transfer (from meter to CMRI /AMR equipment) rate should be minimum 9600 bps.

13.2.	The software shall have provision to indicate no. of Meters data available in CMRI.

13.3	Provisions must be there to limit the load survey data in terms of days when data is being collected by CMRI from the meter i.e., it shall not be a dumped data for 60 days.(The CMRI/BCS software shall request the user to specify the number of days of load survey required before going for reading  the meter data)

13.4	The Software shall have date and time stamp provision whenever downloading of data from Meter.

13.5	The Name Plate details shall be made available whenever downloading is made from the meter i.e., Meter Sr.No, Meter type, Rating, Meter constant and Manufacturing date.

13.6	At any instant of time during communication with CMRI the display should not get disturbed and a suitable indication shall be made available in the Meter display/CMRI that communication has been established with CMRI.

13.7	The calibration software (CMRI) should have testing time of minimum 2 minutes and the parameters Kwh, &Kvah calibrated simultaneously. The start and stop command for calibration shall be instantaneous without any time delay.

13.8	The consumption energy (Kwh, Kvah,kvarh) between start and stop should be displayed in Common Meter Reading Instruments.

13.9	The CMRI software should be compatible to display the instant parameters phase wise voltage, current (With icon for Direction), signed KW & signed PF to conduct power check. During the calibration period it should not be possible for the CMRI to go to power saver/ switch off mode.

13.10	Facility for converting the billing data in the CMRI to ASCII format or any other format specified by the purchaser is to be provided by the manufacturer within 30 days from the date of intimation.

14.0.	Collection of data from CMRI and Meter

a.	Dump Data (All Data)

b.	Billing data

c.	Load Survey

d.	Tamper

e.	Setting

f.	Name plate (Meter Sr.No, Meter type, Rating, Meter constant and Manufacturing date.)

g.	Clear CMRI

h.	Instant parameters

i.	Accuracy Test (on BCS/Laptop)

j.	Uploaded File size display (bytes capacity).

15.0. Programming parameters

1.	Demand Integration period

2.	MD type (KW and KVA) Block method

3.	Lead Kvah (lock and unlock)

4.	MD Reset

5.	TOD Programming

6.	Real Time Clock, Date & Time

7.	Profile Capture period (24hrs-minimum, 90days-maximum)

8.	Reset date and time.

9.	MD reset type Auto

16.0.	The BCS software should be capable of transferring data including load survey & the entire meter data from meter/CMRI within 5 minutes per meter by RS232 port.

16.1.	The BCS software shall have GUI (Graphical User Interface) facility and shall be compatible with Windows Operating Systems.

16.2	The BCS software shall have search facility to access / view Data as per CMRI Id (alpha numeric), Date of reading Meter Serial No. Uploaded data based on weekly and monthly collection   Section wise meters (with assigned code), Subdivision, Division, Circle

16.3	Data of a specific meter related to a specific period by entering from and to dates. In the collected data, one of the meter data is to be transferred to some other file if necessary such provision shall be made available. In the downloaded data consumer details is to be provided as optional.

16.4	The BCS software shall have the facility to display multiple graphs for meter reading uploaded for different period for comparison/ analysis while displaying the load survey graph, the exact value for the particular period shall be displayed with respect to the co-ordinates selected. X & Y axis is to be clearly defined and scaled for easy viewing.

16.5	The facility to have Backup data for future reference in a separate storing device, the data in  BCS shall be compressed in suitable form  for transfer and shall be extracted to view/use the same in future as and when required. This provision shall be made available in the software and demonstrated during inspection/installation. (Similar to zip file format)

16.6	The viewing/printing format has to be provided as per Discom requirement. Alternate formats will not be accepted without prior approval. The printing of formats shall have multiple printing options like paper size, portrait/landscape, etc.

16.7.	The software shall have data export facility to spread sheet format like MS-Excel /Open office without distortion of stored data and should have facility to import consumer database of TSSPDCL.

16.8.	The software shall have facility to analyze data acquired from at least two meters database simultaneously.

16.9 The software shall be capable of opening at least two sessions simultaneously so that one 	session shall access one meter / CMRI and 	another session shall analyze data uploaded 	from another meter.

16.10 	The data already available in the BCS should not be overwritten by new data whenever the same is uploaded.

16.11 	As and when the vendor releases new or latest or advanced versions of Software, the same should be made available to TSSPDCL immediately by default on the release date free of cost. The latest versions should support all existing hardware/meters in the field supplied in this tender and earlier supplies if feasible.

16.12 The above software shall be given with security arrangements and compatible for 	CMRI, 	BCS.

16.13.	The necessary software suitable to ISBM, Common Meter Reading Instrument and BCS for testing to be supplied along with samples. All the data including 	load survey to be provided with print along with 	selection option and 	print setting 	option, the date and time in BCS is in the form of DD/MM/YY & Time: 	HH/MM.

16.14.	The down loaded data in the BCS should not disturbed/erased after reloading of the BCS 	software in the PC/Laptop. The data should 	automatically upload to the meter database.

17.0	Data Security :  The meter manufacturer are responsible for ensuring that the data extracted from the meters using algorithms  in the software/firmware of the meters up to down loading to the BCS/AMR Software remains secure during the process.   Any repairs and recalibration to the meters should be done only at the factory of the meter manufacturers.

18.0.	IRDA Port communication capability:

The meters shall have facility for remote reading through IRDA Communication Port from a minimum distance of 1.5 meters with the help of ISBM (Integrated Spot Billing Machine) to facilitate the utility for auto reading in Power ON/OFF, billing the consumer at spot and downloading of six months of data for future use. The meter shall possess suitable fast and reliable infrared communication for data transfer. There should not be any possibility of tampering of data stored in meter even after getting the password of the software. It should be locked at the time of manufacturing. There should be RTC adjustment/correction. Adequate tamper proofing shall be provided to disallow any change of such auto recorded reading by the meter reader.

18.1.	All sorts of communication between meter and ISBM shall be of “One way” type. Data could only be downloaded from meter to ISBM but no command regarding data alteration in the meter should be possible in any case.

18.2.	The meter shall have capability of IRDA Communication with ISBM (procured separately) and necessary protocol shall be  provided by the bidder compatible to the existing ISBMs being utilized for billing by utility . In such case both meter manufacturer and ISBM supplier shall give an undertaking to utility that they are compatible and able to generate consumer spot bill.

The supplier has to submit the protocols used for IrDA meters to TSSPDCL  so that the meters can be read by common ISBMs / SBMs and the communication protocol of the Three phase IrDA meters is enclosed in the Annexure III(d).

(a) The successful bidder shall submit 1 no sample ISBM of each reputed makes i.e. Lampex & Analogic whose SBMs are in present use in TSSPDCL and also any other reputed makes duly compatible to TSSPDCL tariff regulations.  The ISBM shall be compatible to generate spot bills for Single Phase IrDA & Three Phase  IrDA meters.  Further the successful  firms have to arrange demonstration of

(i) downloading data from IrDA port meters on to the ISBM directly and to generate consumer spot bill for IrDA. The meter manufacturers shall give an undertaking to TSSPDCL that both the meter and ISBM are compatible and able to download the readings from all makes  of Three phase meters. The meter manufacturers should submit an undertaking obtained from ISBM manufacturers that the meter data is accurately downloaded from the meter to ISBM by using TSSPDCL IrDA protocol given in the specification for Three  phase IrDA meters .

(ii) need to demonstrate on field that the billing is done correctly for the existing tariff and the same is to be certified by TSSPDCL/Revenue wing.

iii) the adopted IrDA protocol has to be shared with TSSPDCL and it should be modifiable by the meter manufacturer, as and when required by TSSPDCL without any additional cost.

The Technical specification for ISBM is enclosed vide Annexure – 5 for information and guidance purpose.

  - Parameters to be downloaded with ISBM :

The following parameters should be downloaded by ISBM.

- Meter make

- Meter Sr. No.

- Time & Date

- All the parameters specified in scrolling mode along with tamper indications if any.

- ISBM must have facility to download the above data to the base computer.

Other than above, if manufacturer proposes to record extra parameters, may indicate in their offer.

19.0.	Self Diagnostic Features: The bidder shall provide details of self diagnostic features available and indication on the 3 phase meter for unsatisfactory/non-functioning of the following.

- Time & calendar.

- Real time clock (RTC) battery.

- All display segments

- Non volatile memory.

20.0.	Calibration :

The Meter should be factory calibrated and no modification of calibration should be possible at site by any means what so ever.  This is to ensure that the meter cannot be tampered at site.

21.1.	TOD TIMINGS:

- There shall be provision for at least 8 (eight) TOD time zones for energy and demand. The number and timings of these TOD time Zones shall be programmable.

- It shall be possible to change the different time zones through  RS 232 port even after installation of meter with special software and password protection.

- TOD Timings in six zones by default shall be as given below. However software has to be provided to change the TOD zones whenever required.

TOD 1 - 00.00Hrs. to 06:00Hrs.

TOD 2 - 06.00Hrs. to 10:00Hrs.

TOD 3 - 10.00Hrs. to 14:00Hrs.

TOD 4 - 14.00Hrs. to 18:00Hrs.

TOD 5 - 18.00Hrs. to 22:00Hrs.

TOD 6 - 22.00Hrs. to 24:00Hrs.

Note:	The provision for TOD wise bill point active energy and apparent energy and maximum demand shall be available on meter-display which will be utilised as and when necessity arises. However, same should be logged in the meter memory and be capable of downloading to the BCS through the CMRI and be available for viewing at the BCS end.

22.0.	CONSTRUCTION:

  - Meter shall be designed and constructed to be capable of withstanding all severe stresses and vibration and dust environments likely to be encountered in actual field.  All parts that are likely to develop corrosion shall be effectively protected against corrosion by providing suitable protective coating.  The meter shall have proper fixing arrangement for mounting in meter box.

  - The meter Case shall be made up of unbreakable high grade flame retardant poly carbonate with minimum thickness of 2 mm and of good di-electric & mechanical strength. Meter case and external terminal cover should be injection moulded in UV stabilized poly carbonate. The moulded meter case should not change in colour, shape, size, dimension when subjected to 72HRS on UV Test. It should with stand 650Deg C glow wire test and heat deflection test as per ISO 75. The External Terminal Block Cover shall be kept fully transparent. The meter case and meter cover should be fully transparent, unbreakable UV stabilized poly carbonate for easy reading of all the display values/ parameters and should not fade in course of time and become opaque causing inconvenient in course of time.

22.3  It should be compact and of reliable design to make it immune to vibrations and shocks in normal transportation and should be capable 	of withstanding several stresses likely to 	occur in actual service.  The 	latest state of art technology of surface mounting of 	components etc. may be used for the purpose.  The soldering if any used shall be 	protected against dry solders.

  - The construction of the meter shall be such as to permit sealing of the meter cover, the terminal cover etc. independently.  It should be ensured that the internal parts are not accessible for tampering etc., without breaking the meter cover and meter seals. The meter cover should be ultrasonic Welded with the meter base and there shall not be any fastening arrangements for the same. The ultrasonic welding should be continuous in nature such that no part of the periphery shall be left without bonding. This is to ensure that in case of any attempt to open the cover from the base, there should be visible evidence of opening/tampering.

22.5	Meters shall be designed and constructed providing reinforced insulation in such a way as to avoid 	introducing any danger in use so as to ensure specially.

- Personnel safety against electric shock.

- Personnel safety against effects of excessive temperature.

- Protection against spread of fire.

- Protection against penetration of solid objects, dust and water.

In addition necessary documentary evidence shall be made available by the supplier for having used Industrial Grade components.  Further, meters should be provided with Short circuit current protection .

- Terminals and Terminal block:

  - The terminal block shall be of moulded type and shall be fixed to the 	extended portion of the meter base. The meter base shall cover the 	terminal block of its back and sides. It should be non hygroscopic, non ignitable and with material of good dielectric and mechanical strength. Extended terminal cover shall be provided, to ensure that the internal 	parts are not accessible for tampering etc. without breaking seals.  A firm connection shall be established within the meter to energize the 	voltage circuit. The distance between the end terminal block and the ending of the extended terminal cover shall be a minimum of 2 inches.

  - The terminals in the terminal block shall be of adequate length in order to have proper grip of conductor with the help of screw adjustable metal plates to increase the surface of contact and reduce the contact resistance. The screws shall have thread size not less than M4 and head having 4-6mm. Diameters. The screws shall not have pointed ends at the end of threads. All terminals and connecting screws and washers should be of tinned / nickel plated brass material. The terminal block should withstand glow wire test at 960 + 15 ºC and the terminal should withstand at least 135 ºC. as per IS.

  - Sufficient clearance shall be allowed between terminals.  Further, the supporting webs between the two terminals of the terminal block should be sufficiently high to ensure that the two neighboring terminals do not get bridged by dust or it is not possible to have flash over between adjacent terminals of terminal block.

  - The terminals shall be of suitable rating to carry 150% of Imax of 10-40A and  made of electro-plated (or tinned) brass and shall be of replaceable type.

  - All connection screws and washers should be tinned/nickel plated 	brass.  The terminal screws shall not have pointed end at the bottom.  All terminals will have two screws.  The terminals shall be properly bound in the insulation.  Sufficient clearance can be provided between 	terminals to avoid possible flash over.

  - The terminal block shall have provision with double screws for fixing to the meter board.  It shall not be possible to remove the meter from the 	hanging screw without removing the screws from the terminal block.

  - The extended terminal cover shall be transparent fixed to the meter terminal block by two screws.  The screws should not be detachable 	from the cover and shall have provision for sealing.  The terminal cover extension shall be designed such that cable and cable glands are covered completely inside the box to avoid mishandling of the cables by unauthorized persons.

24.0.	Connection diagram: Every meter shall be indelibly marked with a connection diagram showing the phase sequence for which it is intended and shall be attached to the inner side of the extended terminal cover.  In case any special precautions need to be taken at the time of testing the meter, the same may be indicated along with the circuit diagram. The terminals shall be clearly embossed on terminal block which is visible from distantly on terminal block for giving external connections.  A diagram of connections should be provided inside the cover of terminal block.

25.0.	Terminal Arrangement :  The terminal arrangement and connection diagram shall be marked in accordance with clause 7.2 of IS 13779 . Terminal arrangement shall be in sequence RPh(in), RPh(out), YPh(in), YPh(out), BPh(in), BPh(out), Neutral (in), Neutral(out).

26.0	Fixing arrangement of meter :The meter shall have minimum three fixing holes, one at the top for mounting and two at the bottom, inside the terminal cover. The top hole shall be key-hole type on the back side of the meter base so that hanging screw is not accessible after fixing meter and it shall be not possible to remove the meter from the hanging screw without removing the terminal cover and screws behind the terminal block cover. The lower side fixing holes shall be provided under ETBC. All the fixing holes shall be designed in such a way that once meter is mounted; the screw heads shall not be accessible.

27.0	Non Flammability:  The terminal block, the terminal cover and the case shall ensure reasonable safety against spread of fire.  They shall not be ignited by thermic over load of live parts in contact with them.  To comply with this these parts shall fulfill the conditions of the glow wire test as per CBIP -325.

28.0  Sealing of meter:

i) 	Proper sealing arrangement should be provided on the meter to make it tamper resistant and avoid mishandling by unauthorized persons.  The construction of meter shall be such as to permit sealing of the meter cover in two locations i.e right & left apart from the terminal cover which is detailed elsewhere in the specification.

ii) 	The size of the sealing screw must be in such a way to provide one more AP-PDCL security seal along with company seal in the same screw. The sealing screw should be unidirectional This is to ensure that internal parts are not accessible for tampering without breaking the seals.

iii) 	One number separate sealing arrangement to the MD Reset button and separate flap for RS 232 port shall be provided.

iv) 	Bidder shall provide patented seals as per CEA Regulation(2006)

v) 	The holes for sealing wire shall be minimum 2mm dia .

29.0 Tamper and fraud protection/Monitoring:

29.1	The meter should have tamper and fraud protection features immunity to external disturbances as per CEA installation and operation of meters regulations so as to continue to register active and apparent energy accurately .Some of the conditions are as under .

a)	Phase sequence and Phase Reversal: The meter should record actual consumption correctly irrespective of the phase sequence and phase reversal.

- Current Reversal: Correct energy registration even on current reversal on one or more phases. The reverse indication in the form of blinking LCD phase icon or LED to indicate which phase is reverse. The meter shall record active energy in forward direction even if one or more CT’s are reversed.  The current vector direction shall always be considered as positive ( import)  for the computation of 3 phase active energy which shall be added in the main active energy ( import) register. The meter shall also record apparent energy in forward direction even if one or more CT’s are reversed

- Missing potential: Correct energy registration even on non availability of single or two phases. Meter should remain functional even when either of any phases or any one phase along with neutral is available to the meter and record correct energy.

- The meter shall continue to record energy as per prevailing condition even if the neutral is accidentally or intentionally disconnected.

- The Meter recording should be insensitive to passage of DC voltage or should log as an event in the memory as neutral disturbance. The meter should record energy as per voltage measured between incoming phase and neutral when DC signal/voltage is injected on the neutral through a diode/device. A conformity test on this condition will be carried out at Vref applied between incoming phase and diode terminal.The meter shall be immune to DC in the current range of I basic to I max and in the power factor range of 0.5 lag to 0.5 ld

- Indication to show whether meter records consumption in all the three phases should be available in the display. Non recording consumption in any one of the phase should be indicated.

- The meter shall be immune of any abnormal frequency signal or meter shall log and display as tamper in the event abnormal frequency signal i.e., less than 47.5 Hz or more than 52.5 Hz is supplied to the meter.

- Meter shall record energy accurately under the effect of signals emitted by mobile phone or any other such devices. In conformity of this, the meter shall be checked under such influence (10 minutes) for the following conditions:

10% Ib and UPF, 50% Ib and UPF, Ib and 0.8 PF, 120% Ib and UPF

- The meters shall be immune to tampering through application of external magnetic fields at least up to 0.5 Tesla (DC) and 0.2 Tesla +/- 5% (AC) as per CBIP-325. The magnetic test should be conducted on all three phases.

- On application of magnetic interference beyond 0.2 Tesla, the meter shall record energy up to  150% Imax, rated voltage and UPF as per CBIP-304. The meter is expected to be immune to such interference and this clause is applicable when interference level is beyond immunity offered by the meter. The vendor has to state the level under which meter records energy as stated above.

- The accuracy of the meter should not be affected with the application of abnormal voltage/frequency generating device such as spark discharge of approximately of 35KV.The meter shall be tested by feeding the output after exposing it to the following conditions for 10 minutes:

- On any one of the phase or neutral terminals

- On any connecting wires of the meter

- Voltage discharge with 0-10mm spark gap

- at any place in load circuit

- at proximity of the meter(within 5 cm )

To this effect, a test certificate must be submitted by the bidder from any government approved NABL LAB/CPRI. The accuracy of the meter shall be checked before and after the application of the above device.

Note.1 :    The disturbances to be considered are

- Harmonics.

- Voltage dips and short interruptions.

- Conducted transients.

- D.C. and A.C. magnetic fields.

- Electro Magnetic fields.

- Electro static discharge.

- Radio frequency interference suppression.

Note 2:	Especially, special care should have been taken such that DC & AC magnetic field in proximity of the meter do not damage or influence the meter performance.  Besides, an internal magnetic shield has to be provided in the meters in this regard.

29.2.	Tamper.

1.	Tamper and fraud monitoring should be as per CBIP -304 and also should comply CEA installation and operation of meters regulations.

2.	The tamper indications should be selected and stored in the order of occurrence in three blocks.

3.	In the first block, the voltage missing, voltage unbalance and its date of occurrence and restorations, with date and time should be recorded and stored in respective compartments.

4.	In the second block the tamper indications for other features like current circuit short etc., should be recorded.

5.     In the third block other tampers are to be stored.

29.3	Generally the meter shall have the following special features to monitor/ detect tamper and fraud against meter:

a.	Meter Cover: In the event the meter is forcibly opened, even by 2 to 4 mm variation of the meter cover, same should be recorded as tamper event with date & time stamping and the meter should continuously display that the cover has been tampered. It is suggested that the manufacturer should develop their software such that there will be some time delay for activation of this tamper feature and during that period only the meter cover should be fitted. The delay in activation of software shall be for one instance only. After the meter cover is fitted, it shall get activated immediately without any delay on LCD display in blinking mode so that it is easily noticed by the meter reader. The above tamper shall detectable even in power off condition.  The reset of this tamper event shall be in the scope of the manufacturer only.

b.	Unbalance/Missing Potential :  The meter should be capable of recording occurrence of a missing potential and its restoration with date and time of first such occurrences and last restoration along with total number of such occurrences during the above period  phase wise.

The threshold voltage for voltage missing indication may be 165V for 240 V meters and shall applicable only if phase is available. The threshold voltage for voltage unbalance indication may be 30 % of Vref   between phase to phase and phase to neutral.

c.	Current Unbalance: The meters shall indicate load unbalance over and above 30% between the phases for loads above 10% of Ib.

d.	Current Circuit Short: The meter shall be capable of detecting and recording occurrences and restoration of shorting of any one or two phases of current, with date and time of occurrence  and restoration. Bidders may indicate logic for the above tamper detection and logging scheme.

e.	Magnetic Tamper: The meter should record energy with in specified limit as per CBIP-304 latest amendments in presence of stray magnetic field and record the influence of abnormal magnetic field with date and time in the memory.

f.	Neutral Disturbance: When the neutral from both incoming and    outgoing side are disturbed. Meter shall record correctly in case AC/DC high frequency signal is injected in the neutral circuit of the meter.

Besides the meter shall not display any nuisance tamper information on service conditions such as over compensation, leading PF on one phase and lagging PF on other phase and also switching operation.

The meter manufacturer shall log the tamper events as per the logics and thresholds given by TSSPDCL which are given below

| 3-Ph WC Solar Net Energy Meters |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Sl. No. | Type of tamper | Requirement | Occurrence |  | Restoration |  |
|  |  |  | Voltage | Current | Voltage | Current |
| 1 | Missing Potential | Phase Wise | Vx<10% of Vref irrespective other phase Voltage. | lx > 2% Ib Where x is Tampered Phase | Vx>40% Vref irrespective to any other phase | - |
| 2 | High Voltage | - | > 115% of Vref | - | <110% of Vref. | - |
| 3 | Low Voltage | - | 0 > Vref<75% of Vref. | - | >80% of Vef. | - |
| 4 | Potential Unbalance | - | (Vmax-Vmin) > Threshold value of Vef. (10%) | No minimum Current Reqd | (Vmax-Vmin) < Thrshold value of Verf. (10%) | No minimum Current Reqd |
| 5 | Over Current | - | - | >6 times of Ib | - | <6 times of Ib |
| 6 | Current Unbalance | - | - | (Imax - I min)>50% Ib | - | (Imax - I min)<50% Ib |

| 7 | Low PF | - | - | lr or ly or lb > 5% Base Current with PF < 0.5 | - | lr or ly or lb > 5% Base Current with PF > 0.5 |
| --- | --- | --- | --- | --- | --- | --- |
| 8 | Current Reversal | Phase Wise | - | lx>5% Base Current, direction of current reverse and PF value > 0.2 | - | lx>5% Base Current, direction of current forward and PF value > 0.2 |
| 9 | CT Missing | Phase Wise | Vref > 10% of Vref. | lx<1% of Base Current & in other 2 phases Ix>10% of Ib. | Vref > 10% of Vref. | lx>10% of Base Current |
| 10 | CT Open | Phase Wise | - | Ix<2% of base current & in other 2 phases Ix>10% of Ib | - | Avg Current of all 3 phases > 10 % of I basic |
| 11 | CT By-pass | - | - | Vector sum of (Ir+Iy+Ib-In) > 10% Ib & Iph > 2%Ib in all phases | - | Vector sum of (Ir+Iy+Ib-In) < 10% Ib & Avg Current of all 3 phases > 10 % of I basic |
| 12 | Magnetic Tamper | - | - | - | - | No minimum Current Reqd |
| 13 | Power OFF | - | V=0 in all three phases | - | - | - |
| 14 | Meter Cover Open | - | - | - |  |  |
| 15 | Invalid Voltage | - | PT missing event should not persists. Phase angles deviated >±10° from their respective fundamental values. | - | Phase angles deviated <±10° from their respective fundamental values. | - |
| 16 | Neutral Disturbance | (a) Chopped Signal- if any spurious signal injected to the neutral of meter, either offered meter will be immune or if gets affected it will log the event & register energy on reference voltage, actual current & UPF. B) If any one of the phases and neutral get interchanged the accuracy should not be affected and it shall be immune and also it should log the event with snap shot |  |  | When normalcy obtained. | - |

| 17 | Invalid Phase Association | - | When voltage & current sequence is different. | - | When voltage & current sequence is same. | - |
| --- | --- | --- | --- | --- | --- | --- |

29.4.	The No. of tamper information / events for each type of tamper to be recorded in three blocks under each category is as follows:

Block I:

1.	Voltage missing (50)

2.	Voltage unbalances (30)

Block II:

3.	Current unbalance (50)

4.	Current circuit short (10)

Block III:

5.	Software (settings and parameters) change – (10) events with date and time along with parameter changed.

6.	Neutral Disturbance (9).

7.	Cover opening (1).

8.	Magnetic influence events (10)

9.	Power failure (30)

29.5. A minimum of 200 tamper information (FIFO basis) shall be available in the memory for retrieval from the meter at any time. The above tamper in EACH	BLOCK information is of First In First Out basis but the first tamper occurrence with date should appear till the tamper persist.

29.6.	Tamper Information:

After occurrence of any tamper, the tamper display should appear in the display and the tamper data should remain in memory so that the occurrence of latest tamper can be retrieved and also seen in the display at any time.

29.7. 	Provisions should not be there to clear the tamper information through CMRI or any 	other means. Provisions should be made such that first occurrence of tamper should exist 	as long as tamper exist in the 	circuit.

29.8. 	The persistence time for detecting any abnormality shall be 300 seconds for occurrence and for restoration & it shall be 30 seconds for meter cover opening, Magnetic interference and Neutral disturbance.

29.9	In BCS the snap shot feature is to be provided for every meter tamper data with cumulative Kwh(I&E), Kvah(I&E), Voltages, currents & Date & time at the time of the tamper occurrence & tamper restoration. A summary report on tamper events along with its total duration for each type of the events occurred from the date of manufacturing or installation is to be made available as detailed in Sub Annexure-1.

29.10 The Supplier should furnish the details as to how their meter is able to detect/ protect 	/ recording the above tamper and fraud features with sketches and phase diagram.

30.0.	Responsibility:

30.1.	The  software suitable to Common Meter Reading Instruments & ISBMs shall be provided with ordered meters to Common M.R.I/ISBMs manufacturer approved by Board as detailed in CBIP - 304 and as detailed elsewhere in the Purchase Order.

30.2	Besides, they should supply the communication cable for downloading the data from meters with RS 232/RJ11 port terminating into a 9 pin ‘D’ type male connector with a cable of minimum 1000 mm +/- 10 mm length at free of cost at for every 500 meters lot for down loading the data to Common Meter Reading Instruments along with the supplies of meter, failing which the supply will not be taken into stock.

30.3	A detailed list of bought out items which are used in the manufacturing of the meter should be furnished indicating the name of firms from whom these items are procured is to be submitted along with the technical bid.

30.4	The meter shall be completely factory sealed except the terminal block cover. The provision shall be made on the Meter for only two seals to be put by utility user. The Terminal cover should be transparent with one side hinge with sealing arrangement.

31.0	Technical specification for pilfer proof box to house the meter.

    - The box shall be weather proof made out of transparent Polycarbonate with flame retardant properties.

    - It shall be capable of withstanding temperatures of boiling water for 5 minutes continuously without distortion or softening.  The thickness of the box shall not be less than 3mm on the load bearing side (i.e., back side of the box) and other sides, door and roof shall not be less than 2.5mm. The box shall have its roof tapering down to both sides for easy flow of water.

    - The Boxes shall generally comply with the provisions of IS 5133 and IEC60 695.  The boxes shall be suitable for outdoor/indoor application.  The outdoor box shall have its roof designed for easy flow of rain water without any stagnation on the box.  The box shall be with good workmanship.

    - The dimensions of the box shall be such that there is a minimum clearance of 50 mm on all sides, 25mm clearance on the front and 10mm on the back of the meter then the meter is fixed in the box.

    - Soft rubber gaskets shall be provided all around wherever required for protection against entry of dust and water.  It shall comply with IP-33.Cable tie glands shall also be provided at the incoming and outgoing entry of service wires below the terminals

- Colour : Fully transparent

- The contents of the box are as follows

vi	Internal hinges :  A minimum of 2 nos. internal hinges well protected against corrosion shall be provided.  The hinges of the door should be concealed and they shall be fixed to the flanges provided to the base and cover of the box in such a manner that the door opens by a minimum of 120 degrees.

vii	Handle :  Suitable handle or knob shall be provided for opening of the box door.

viii	 Fixing arrangement :  The meter  base supports inside the box are raised by about 10 mm in the box for ease of wiring.  While fixing the meter screws should not protrude outside.  For fixing the box to wall or wooden board 4 nos. key holes of minimum 6 mm dia shall be provided at the four corners of the meter box. The meter is to be installed in the box and the box in the assembled condition shall have provision to fix it to a pole or on wall.

xix	Latch : The door shall be provided with a GI latch or a ‘U’ clamp to secure it with the base of the box.

x	Sealing arrangement : The box shall have provision for 	minimum 2 nos. seals to make it fully tamper resistant.

xi	Inlet Outlet:  Suitable circular holes shall be provided on the left of the box for inlet/right side of the box for outlet with brass or fire resistance high grade engineering plastic glands securely fixed to the box on both sides by check nuts.  The incoming and outgoing cables shall be clamped to the inside base of the meter box to ensure fixing of the cable.  Cable glands shall be collapsible type so that there shall be no gap after tightening.

xii	Printing : The letters “TSSPDCL” and the P.O. No. and date shall be engraved / etched on Metallic lable fixed on the top 	cover of the box.  The name of the manufacture shall be	engraved on the bottom half of the box.  A blank sticker shall 	also be fixed on the meter box for use of field staff to indicate Service No. etc.

xiii 	The fixing arrangements shall not be complex and it shall be easily approachable for connections when the door is open and is completely tamper resistant once it is sealed.

xiv	The dimensional drawing giving details of meter box shall be enclosed in the bid.

32.	Guaranteed technical particulars:

The guaranteed technical particulars as detailed in the specification Annexure-III (a)  & III (b) shall be guaranteed and a statement of guaranteed technical particulars shall be furnished in the format along with the bid without which the Bid will be treated as Non-Responsive.

32 	TESTS:

32.1	Type tests :

32.2	Meters:

The type test certificates for all tests as per IS: 13779-1999/ Relevant IEC Standard (latest amendments) will be furnished along with tender. Type test certificates from any one of the standard laboratories such as NPL/CPRI/ NABL accredited govt laboratories alone shall be considered.

The type test reports can pertain to similar type of materials with similar or higher capacity current rating. One copy of type test reports shall be furnished with the Bid.  The date of type tests shall be not older than 3 years from the date of opening of the tender. The type testing should be on three samples if type test reports submitted are as per IS: 13779/99 or on one or more samples if the type test reports submitted are as per CBIP No. 325 The Bids received without type test reports will be treated as Non-responsive.

32.3	Additional type tests

In addition to the test mentioned in 13.1.1, above the supplier shall have to furnish the following type test reports:

  - DC influence test as per IS: 13779-1999 or IEC 62053-21 in phase circuit

  - The test of influence of supply voltage shall be carried out as per clause No.12.7.2.1 of IS: 13779-1999 except the interruption time should be variable from 10 msec to 5 sec instead of fixed time.

  - Test of voltage variation as per this specification

  - Compliance of anti-tamper features as per this specification

  - The meter shall withstand impulse voltage test at the rated impulse voltage of 10 kV  as per IEC 62052-11:2003

  - External AC/DC magnetic influence test as CBIP -325.

g. 	A 35 KV Spark discharge test certificate must be submitted by the bidder from any Government NABL/CPRI Lab as per clause no10.1.K.The accuracy of the meter shall be checked before and after the application of the above device.

32.4. The type test certificates of the above additional tests shall also be submitted along with 	the bid. The following information should be clearly mentioned in the type test reports.

i)	Type of display

ii)	Details of Shunts/CT used in main neutral circuit

iii) 	Accuracy at different loads and PF for all phases separately.

The bid will be made non-responsive if the bidder fails to furnish the above type tests and additional type tests reports not more than 3 years old on the date of bid submission.

  - Tests for boxes: The following tests are to be conducted on the box at any independent laboratory and test reports are to be furnished along     with tender schedule. Manufacturing shall be started after approval of test reports and drawing approval.

- Test of material identification

- Test for mechanical strength as per IS 14772.

- Test for water absorption as per IS 14772.

- Test for stability at high temperature as per IS 14772.

- Test for withstanding temperature boiling water for 5 minutes continuously for non-distortion or softening of material as per IS 14772.

- Glow wire test as per CBIP Technical Report No.304.

33.	Acceptance and routine tests.

33.1	Meters

33.1.1. Acceptance Tests:

Samples picked up by the inspecting officer for acceptance tests shall be first subjected to ‘soaking’ at 70 +/- 2 Deg. C for four hours.  After normalizing the acceptance tests as stipulated in CBIP (with latest amendments) and IS shall be carried out by the supplier in presence of purchaser’s representative.  Also the following additional tests are carried out on mutually agreed quantity of meters from each lot offered for inspection.

- Shock Test.

- Vibration Test.

- Magnetic induction of external origin (AC&DC).

- Tamper & Fraud protection as specified in this specification

- Voltage variation test as per this specification

- Test of no load condition at 70% and 120% of rated voltage. The minimum test period shall be as per cl- 8.3.2 of IEC: 62053-21-2003.

- Test of DC components in AC circuits – The limits of variation in percentage error shall be 3.0% for class 1 meter at Imax/sq.root of 2 and UPF as per IS:13779. The meter shall also measure energy within the above limits in the current range of I basic to I max and p.f. 0.5 lag to 0.5 lead.

- Diode injection test.

- Accuracy test under the anti tamper conditions as specified in this specification.

- Test for least count.

- Test for time taken for down loading data to CMRI & to BCS.

- Test on communication capability & software compliance.

- Verification of tamper logics and verification of display parameters.

- Permanent magnet test.

- Test of application of abnormal voltage/frequency generating devices as per this specification.

- Additional acceptance tests shall include Surge withstand (SWC), Lightning impulse and HF disturbance as per IEC 62052-11. For these specific tests, one sample meter per order from one of the offered lot shall be subjected to SWC/other semi-destructive tests. Meters after tests shall not be used

For sampling plan for pre-dispatch inspection, maximum lot size of 10,000 meters shall be considered for acceptance test as per IS:13779/99.

33.1. 2. Routine Tests:  All the routine tests as stipulated in IS  and  in addition tamper and fraud protection tests as specified in the specification. shall be carried out and test certificates shall be furnished for approval of the purchaser.

33.1.3. The routine test certificates for the following shall be furnished    for approval of the purchaser.

- Physical verification of dimension of the box.

- Compatibility of the box for housing the meter ensuring ease of connecting and the reading the meter.

34.0	Test Reports / Test Certificates:

34.1	Record of routine test reports shall be maintained by the Bidder at his works for periodic 	inspection by the purchaser’s representative.

  - . Test certificates of tests conducted during manufacture shall be maintained by the Bidder.  These shall be produced for verification as and when desired by the purchaser.

35.0.	Test Facilities:

The tests shall be carried out as per relevant Standards and test certificates shall be furnished for approval.  The Bidder shall indicate the details of the equipment available with him for carrying out the various tests as per relevant Standards.  The bidder shall indicate the sources of all materials.

Note: The Meters used for conducting tests shall be calibrated periodically at reputed Government Accredited Test Laboratories and test certificates shall be available at works for verification by  purchaser’s representative.

36.0. 	Inspection:

36.1	The inspection may be carried out by the purchaser at any stage of manufacture. The manufacturer shall grant free access to the purchaser's representative at a reasonable time when the work is in progress.   Inspection  and  acceptance  of  any equipment under this  specification  by  the purchaser,  shall not relieve the supplier of his  obligation  of  furnishing  the equipment   in accordance with  the  specification  and shall not prevent subsequent rejection if the equipment is  found to be defective.

36.2	All acceptance tests and inspection shall be made at the place of manufacturer unless otherwise especially agreed upon by the Bidder and purchaser at the time of purchase. The Bidder shall afford the inspector representing the purchaser all reasonable facilities without charge, to satisfy him that the equipment is being furnished in accordance with this specification.

36.3	The supplier shall keep the purchaser informed in advance, about the manufacturing programme so that arrangement can be made for inspection.

36.4	The purchaser reserves the right to insist for witnessing the acceptance/routine testing of the bought out items. The supplier shall give 15 days for local supply/30 days in case of foreign supply advance intimation to enable the purchaser to depute his representative for witnessing the acceptance and routine tests.

36.5	The purchaser reserves the right to get type test any meter, or Box from any of the lots offered for inspection received at any Destination Stores at purchaser’s expenses and clause 8.0 (Section-V) applies for any failure to pass tests.

36.6 	NOTE FOR FOREIGN BIDDERS: The Bidder shall indicate the name (s) of reputed inspection agencies and the inspection charges clearly for each lot.  The inspection charges will be borne by the supplier.  However the purchaser reserves the right to appoint at his cost any inspection agency to carry out the inspection.

Training: Training for two of purchaser’s engineers shall be imparted by the bidder.  All expenses towards training of purchaser’s engineers shall be borne by the bidder.   The expenditure towards travel and incidentals including accommodation is to purchasers account.

- 37.0.	Testing after receipt at stores:-

From meters supplied to Stores, TSSPDCL will pick up samples at random @ 1 No. meter for every lot of 5,000 Nos. or part thereof. These samples will be tested for acceptance tests as decided by TSSPDCL at NABL Accredited Government Laboratory in the presence of representatives of supplier and TSSPDCL as per relevant IS/IEC/CBIP and TSSPDCL specifications at suppliers cost. The samples of subsequent lot shall be tested at different NABL Accredited Government Laboratories. If the sample meter fails in the testing again two sample meters will be picked up at random from the stores and tested.  If the meter fails in the above tests the entire lot will be rejected. If acceptance test fails in subsequent lots, the PO will be terminated. All the expenses for testing of the meters shall be borne by the supplier.

38.0  	QUALITY ASSURANCE PLAN :

38.1	The Bidder shall invariably furnish the following information along with his bid, failing which his bid shall be liable for rejection.  Information shall be separately given for individual type of material offered.

- The structure of organization.

- The duties and responsibilities assigned to staff ensuring quality of work.

- The system for purchasing, taking delivery and verification of materials.

- The system for ensuring quality of workmanship.

- The quality assurance arrangement shall conform to relevant requirements of ISO 9001 or 9002 as applicable.

- Statement giving list of important raw materials names of sub-suppliers for the raw materials, list of standards according to which the raw materials are tested.  List of test normally carried out on raw materials in presence of Bidder's representative, copies of test certificates.

- Information and copies of test certificates as in (i) above in respect of bought out accessories.

- List of manufacturing facilities available.

- Level of automation achieved and list of areas where manual processing exists.

- List of areas in manufacturing process, where stage inspections are normally carried out for quality control and details of such tests and inspections.

- Lists of testing equipment available with the bidder for final testing of equipment specified and test plant limitation.  If any, vis-a-vis the type, special acceptance and routine tests specified in the relevant standards.  These limitations shall be very clearly brought out in schedule of deviations from specified test requirements.

  - The contractor shall within 30 days of placement of order, submit following information to the purchaser.

- List of raw materials as well as bought out accessories and the names of sub-suppliers selected from those furnished along with offers.

- Type test certificates of the raw materials and bought out accessories if required by the purchaser.

- Quality assurance plan (QAP) with hold points for purchaser's inspection.  The quality assurance plan and purchasers hold points and notification points shall be discussed between the purchaser and Bidder before the QAP is finalized.

38.3.	The contractor shall operate systems which implement the following.

- Hold Point: A stage in the material procurement or workmanship process beyond which work shall not proceed without the documental approval of designated individuals or organizations. The purchaser’s written approval is required to authorize work to progress beyond the hold points indicated in approved quality plans.

- Notification Point: A stage in material procurement or workmanship process for which advance notice of the activity is required to facilitate witness.  If the purchaser does not attend after receiving documented notification in accordance with the agreed procedures and with the correct period of notice then work may proceed.

38.4.	The contractor shall submit the routine test certificates of bought out accessories and central excise passes for raw material at the time of routine testing if required by the purchaser and ensure that the Quality Assurance requirements of this specification are followed by the sub-contractors.

38.5.	The quality assurance programme of the contractor shall consist of the quality system and quality plans with the following details.

- Quality System:

- The structure of the organization

- The duties and responsibilities assigned to staff ensuring quality of work.

- The system for purchasing, taking delivery and verification of materials.

- The system for ensuring quality workmanship.

- The system for control of documentation.

- The system for the retention of records.

- The arrangement for the contractor’s internal auditing.

- A list of the Administration and work procedures required to achieve and verify Contract’s quality requirements. These procedures shall be made readily available to the project Manager for inspection on request.

(ii)	 Quality Plans:

- An outline of the proposed work and programme sequence.

- The structure of the contractors organization for the contract.

- The duties and responsibilities assigned to staff ensuring quality of work.

- Hold and Notification points.

- Submission of Engineering documents required by the specification

- The inspection of materials and components on receipt.

- Reference to the Contractor’s Work Procedures appropriate to each activity.

- Inspection during fabrication / Construction.

- Final Inspection and test.

39.0. Documentation:

39.1 	All drawings shall conform to International Standards Organization (ISO) `A' series of drawings sheet/India Standards Specifications IS:656.  All drawings shall be in ink and suitable for micro filming.  All dimensions and data shall be in S.I. Units.

39.2	List of drawings and documents:

The bidder shall furnish the following along with bid

- Two sets of drawings showing clearly the general arrangements, fitting details, electrical connections etc.

- Technical leaflets (user manual) giving operating instructions.

- Three copies of dimensional drawings of the box for each quoted item.

39.3	The manufacturing of the equipment shall be strictly in accordance with the approved drawings and no deviation shall be permitted without the written approval of the purchaser. All manufacturing and fabrication work in connection with the equipment prior to the approval of the drawing shall be at the supplier's risk.

  - Approval of drawings/work by purchaser shall not relieve the supplier of his responsibility and liability for ensuring correctness and correct interpretation of the drawings for meeting the requirements of the latest revision of application standards, rules and codes of practices. The equipment shall conform in all respects to high standards of engineering, design, workmanship and latest revisions of relevant standards at the time of ordering and purchaser shall have the power to reject any work or materials which, in his judgment is not in full accordance therewith.

39.5	The successful Bidder shall, within 2 weeks of notification of award of contract, submit three sets of final versions of all the drawings as stipulated in the purchase order for purchaser's approval. The purchaser shall communicate his comments/approval on the drawings to the supplier within two weeks. The supplier shall, if necessary, modify the drawings and resubmit three copies of the modified drawings for their approval.  The supplier shall within two weeks, submit 3 prints and two good quality report copies of the approved drawings for purchaser's use.

39.6	Eight sets of operating manuals/technical leaflets shall be supplied to each consignee for the first instance of supply.

  - One set of routine test certificates shall accompany each dispatch consignment.

  - The acceptance test certificates in case pre-dispatch inspection or routine test certificates in cases where inspection is waived shall be got approved by the purchaser.

40.0.	Sample:

2 Nos. sample meters shall be submitted along with the bid.   The sample meter shall be provided 1 No. company seal to meter cover.  Tenders received without samples will be rejected.  The samples shall be type tested as per CBIP TR No. 88 / 304 (with latest amendments) and/or IS:13779/1999  applicable.  The sample shall comply with the specification.

The software for CMRI & BCS and memory mapping including communication probe should be submitted along with offer for testing the sample meter.

The sample meter shall comply with all tests in all respect to this 	specification. In case 	sample meters are found not conforming to the requirements both in hardware and soft 	ware, the price bid of the offer shall not be opened and offer will be rejected.

A team of officers will also be deputed to the factory premises of the bidder to assess the manufacturing quality and facility and to pick up two more samples of the same range/similar specification from the manufacturing line or from the storage place for testing at CPRI at bidder’s cost before or after placing order. In case sample meters are found not conforming to the requirements both in hardware and soft ware, the purchase order will be cancelled and the vendor will be black listed.

The time required for down loading the data as confirmed by the bidder will also be tested at testing lab.

After six months of installations of the meters of the successful bidders, meters in premises of consumers, will be released and taken out for testing in NABL accredited Govt laboratories at the cost of TSSPDCL. The bidder’s representative can also be present at the time of release and testing of meters. If the meters are found to be defective such supplies will be closed, B.G invoked and EMD forfeited. The firm will not be eligible for participating for any tender in TSSPDCL for the next three years.

41.0 	Packing & Forwarding:

41.1	The equipment shall be packed in crates suitable for vertical/horizontal transport as the case may be, and suitable to withstand handling during transport and outdoor storage during transit.  The supplier shall be responsible for any damage to the equipment during transit, due to improper and inadequate packing.  The easily damageable material shall be carefully packed and marked with the appropriate caution symbol.  Wherever necessary, proper arrangement for lifting, such as lifting hooks etc., shall be provided.  Any material found short inside the packing cases shall be supplied immediately by supplier without any extra cost.

41.2  	Each consignment shall be accompanied with a detailed packing list containing the following information.

a.	Name of the consignee.

b.	Details of consignment.

c.	Destination.

d.	Total weight of consignment.

e.	Handling and packing instructions.

f.	Bill of Material indicating contents of each package.

41.3  	The supplier shall ensure that the packing list and bill of material are approved by the purchaser before dispatch.

41.4	The packing shall be done as per the manufacturer's standard practice.   However, he should ensure the packing is such that, the material should not get damaged during transit by Rail/Road.

41.5  	The marking on each package shall be as per the relevant Standards and shall also contain.

42.0  	Supervision Services:  Nil.

The Purchaser will arrange for unloading of the consignments at the destination stores.

43.0 	Mandatory spares & Tools:

The bidder shall give the list of items and shall keep a reasonable stock of the same, during the warranty period.

44.0	Technical deviations:

Any deviation in Technical Specification as indicated in the format shall be specifically and clearly indicated in the schedule of deviation format .

45.0	Guarantee:

The material should be guaranteed for satisfactory operation for a period of 5 years from the date of receipt of material at destination stores by the consignee in good condition. During the guarantee period if the meter while in its normal operation is found defective, it shall be replaced by the supplier with a new meter free of cost within 15 days. If the meter is not replaced within 30 days of intimation the supplier should note that the guarantee period will be extended to that extent by the number of days delayed beyond 30 days. If the tenderer does not replace within 180 days the cost of the meter(s) will be recovered from the existing bills/ future bills/ Bank Guarantees available TSSPDCL.

Performance guarantee/security: The bidder has to give a guarantee of 10% of the contract value towards performance. If the Supplier fails to deliver any or all of the Materials/equipment or to perform the Services within the period(s) specified in the Contract, the Purchaser will, without prejudice to its other remedies under the Contract, deduct from the Contract Price, as liquidated damages, a sum equivalent to 0.5% per week on the undelivered portion subject to a maximum of 5% of the cost of the undelivered portion within scheduled time. Once the maximum is reached the Purchaser may consider termination of the contract.

46.0	General:

a)	Principle of operation of the meter, outlining the methods and stages of computation of various parameters starting from input voltage and current signals including the sampling rate if applicable shall be furnished by the bidder.

b)	The bidder shall indicate the method adopted to transform the voltage and current to the desired low values with explanation on devices used such as CT, VT or Potential divider as to how they can be considered superior in maintaining ratio and phase angle for variation of influence quantities during its service period.

c)	The bidder shall furnish details of memory used in the meter.

d)	Details of testing facilities:

The manufacturer laboratory must be well equipped for testing of the meters. They must have computerized standard power source and standard equipment calibrated not later than a year (or as per standard practice). The details of testing facilities available for conducting (a) The routine tests and (b) Acceptance tests shall be furnished in a statement. Bids without these details will be treated as Non responsive.

ANNEXURE – III(a)

GUARANTEED TECHNICAL PARTICULARS FOR METERS

| Sl.No | Technical Particulars | Details |
| --- | --- | --- |
| 1 | Make & Type |  |
| 2 | Applicable standard is 13779/1999 (amended up to date) – y/n |  |
| 3 | Accuracy class 1.0 – y/n |  |
| 4 | Rated voltage 3x240 v(+20% to -40%) – y/n |  |
| 5 | Basic current (ib) 5 amp – y/n |  |
| 6 | Maximum continuous current(Imax) 45 A– y/n |  |
| 7 | Starting current 0.2 % of Ib – y/n |  |
| 8 | Short time over current 30 Imax – y/n |  |
| 9 | Display provided with backlit LCD type– y/n |  |
| 10 | Seven number of digits – y/n |  |
| 11 | Size of digits 10x5 mm minimum |  |
| 12 | Power consumption of voltage circuit 1W, 4VA – y/n |  |
| 13 | Power consumption of current circuit 1VA for ct/shunt – y/n |  |
| 14 | Kva/Kw MD provided – y/n |  |
| 15 | Integration period of MD 30 min – y/n |  |
| 16 | Rs232 communication port provided – y/n |  |
| 17 | Material of base and cover polycarbonate – y/n |  |
| 18 | All anti-tamper features as per tender spec are provided – y/n |  |
| 19 | Type of backup power provided -super capacitor(y/n) |  |
| 20 | For internal battery/super capacitor activation push button is provided – y/n |  |
| 21 | Provision of MD reset (auto) with monthly/even/odd month reset date and time – y/n |  |
| 22 | Extended transparent terminal block cover (50mm) is provided with logo & sealing arrangement – y/n |  |
| 23 | Guarantee of five years from date of receipt at stores is complied – y/n |  |
| 24 | Minimum internal diameter of terminal holes 8.5mm – y/n |  |
| 25 | In-house testing facilities for conducting acceptance tests as per IEC / IS and this specification – y/n |  |
| 26 | Availability of calibrated ERS meter of class 0.05-0.1 accuracy with valid calibration certificate – y/n |  |
| 27 | Data retention for a long period (10 years) under power off condition – y/n |  |
| 28 | Four decimal resolution in calibration mode – y/n |  |
| 29 | Icon for current reversal, phase wise – y/n |  |
| 30 | Fixing arrangement of meters as per spec– y/n |  |
| 31 | Furnish principle of operation of meter outlining the methods and stages of computations of various parameters starting from input voltage and current signals including sampling rate if applicable.(as a document hard & soft copy) y/n |  |
| 32 | Manufacturing activities as per specification submitted (details shall be submitted separately in sealed cover along with the offer) |  |
| 33 | Whether type tested – y/n |  |
| 34 | Type test report no |  |
| 35 | Whether QAP submitted - y/n |  |
| 36 | RTC temperature compensated 0-50˚c – y/n |  |
| 37 | Facility for correcting RTC drift thro CMRI/Remote – y/n |  |
| 38 | RTC make & Accuracy (minutes/year) |  |
| 39 | PCB is manufactured by SMT and without any wire loops and joints - y/n |  |
| 40 | TOD time zones are provided for energy & demand as per specification - y/n |  |
| 41 | Internal battery guarantee/undertaking is submitted - y/n |  |
| 42 | Whether voltage & current circuit are solidly connected inside the meter body without any links - y/n |  |
| 43 | Whether type test reports,manual along with copy of the same in two CDs is submitted - y/n |  |
| 44 | Sample meters as per tender documents are submitted out of these one samples should be without ultrasonic welding to confirm constructional features of the meters- y/n |  |
| 45 | As per technical specification spark discharge test at 35 kv is carried out - y/n |  |
| 46 | As per technical specification least count test is carried out – Y/N |  |
| 47 | Details of CT/shunt provided - y/n |  |
| 48 | Number of pulses/Kwh&Kvarh count (p.u) |  |
| 49 | Time taken to function upon powering up of meter |  |
| 50 | Details of terminal blocks provided A) glow wire test of polycarbonate is carried out - Y/N |  |
| 51 | Memory capacity in MB. |  |
| 52 | Non volatile memory retention time in absence of power |  |
| 53 | Over all dimensions & weight |  |
| 54 | Sealing provision for cover, terminal cover, communication port - y/n |  |
| 55 | Protection from lightning & HV surge - y/n |  |
| 56 | Range for safe operation |  |
| 57 | Total number of tamper events available |  |
| 58 | CMRI/BCS software as per specification - y/n |  |
| 59 | Availability of self diagnostic features - y/n |  |
| 60 | Value upto which meter can withstand direct current in AC circuits without getting CT saturated resulting in measurement error of more than permissible limit |  |
| 61 | Magnetic immunity level for AC/DC |  |
| 62 | Compliance to protection from tamper& fraud - y/n |  |
| 63 | Whether the meter can record energy as per voltage measured between incoming phase & neutral terminal when dc signal is injected on neutral terminal through a diode - y/n |  |
| 64 | Availability of SMT manufacturing at the works - y/n |  |
| 65 | Availability of in-house design, development & manufacturing facilities-y/n |  |
| 66 | PCB material glass fr-4 grade (yes/no), if no furnish details |  |
| 67 | Short time over current withstands capacity for one half cycles at reference frequency-(in terms of i-max.) |  |
| 68 | Display sequence as per specification - y/n |  |
| 69 | reading provided in the meter is direct - y/n |  |
| 70 | Confirmation to the effect that meter does not get damaged even if 500v (ac) is applied for 5 minutes between phase and neutral and continue to record correctly after restoration of normal supply - y/n |  |
| 71 | Can meter perform within class 1.0 accuracy upto 600% Ib for pf range 0.5 lag, 0.8 lead & unity - y/n |  |
| 72 | Whether meter can record energy if voltage falls upto 50% of rated voltage at Ib to Imax - y/n |  |
| 73 | Power consumed for display during power off condition (w) |  |
| 74 | Degree of protection ip-51 - y/n |  |
| 75 | Data transfer time a. meter to cmri (min). b. cmri to bcs (min). c.meter reading to ISBM |  |
| 76 | Parameters Logged |  |
| 77 | No. days of Load survey |  |
| 78 | Daily Energy snap - Parameters - No. of days |  |
| 79 | Type of communication - IrDA communication port - RS 232 port |  |
| 80 | Capability of Tamper and fraud prevention & detection |  |
| 81 | Event logging Current related event Voltage related event Others Power ON / Off events |  |

ANNEXURE – III (b)

TECHNICAL PARTICULARS OF BOX

| Sl. No. | Characteristics |  |
| --- | --- | --- |
| I. 1. | # Manufacturer’s name |  |
| 2. | Material used for box body |  |
| 3. | Material withstanding temperature |  |
| 4. | Dimensions of box (l x w x h) |  |
| 5. | # Thickness (mm) |  |
| II. 1. | Color |  |
| 2. | No. of Hinges |  |
| 3. | Handle provision |  |
| 4. | Sealing Arrangements |  |
| 5. | Inlet & Outlets |  |
| 6. | Gasket - Whether gasket is provided for door - Material of the gasket |  |
| 36. | Suitable for outdoor installation |  |

ANNEXURE – III ©

COMPONENT SPECIFICATIONS AND MANUFACTURERS:

All the materials and electronic power components used in the manufacture of the meter shall be of highest quality and reputed makes like given as under so as to ensure higher reliability and sustained accuracy.

1.	 Current Transformers:

The Meters should be with the current transformers as measuring elements.  The current transformer should withstand for the clauses under 5&9 of IS- 13779 /1999 The current transformer should withstand for the clauses under 5&9 of IS-13779 /1999.

2.	Measurement or computing chips:

The measurement or computing chips used in the Meter should be with the Surface mount type along with the ASICs.

USA		:	Teridian, Anolog Devices,Cyrus Logic,Atmel, Philips Dallas, ST, Texas Instruments ,Renesas

Germany		:	Siemens

South Africa		:	SAMES

Japan 		:	NEC

Taiwan		:   Prolific Technology

3.	Memory chips:

The memory chips should not be affected by external parameters like sparking, high voltage spikes or electrostatic discharges. Meter shall have non volatile memory (NVM). No other type of memory shall be used for data recording and programming. (The life of the NVM is highest) There shall be security isolation between metering circuit, communication circuit, and power circuit.

USA	:	Teridian, Atmel, National Semiconductors, Texas Instruments, Philips, ST, Renesas, Microchip.

Japan	:	Hitachi

Germany	:	Siemens

Taiwan	  :  	 Prolific Technology

4.	Display modules:-

a)	The display modules should be well protected from the external UV radiations.

b)	The display visibility should be sufficient to read the Meter mounted at height of 0.5 meter as well as at the height of 2 meters (refer 3.2 d for Viewing angle). c)The construction of the modules should be such that the displayed quantity should not disturbed with the life of display .d) It should be trans reflective HTN or STN type industrial grade with extended temperature range.

Hongkong		:	Genda

Singapore		:	Bonafied Technologies,Holtek,Haijing.

Korea			:	Advantek

Japan			:	Hitachi,Sony.

Taiwan		:	Prolific Technology

5.	Communication Modules:

Communication modules should be compatible for the two ports (one for IRDA port for communication with meter reading instruments & the other for the hardwired RS-232 port to communicate with various modems for AMR).

USA			:	National Semiconductors HP, Optonica, 							Agillant,Texas  Instruments, Maxim.

Holland / Korea	:	Phillips

Japan 			:	Hitachi

Taiwan			:	 Ligitek, Everlight, Prolific Technology

6. Power supply:

The power supply should be with the Capabilities as per the relevant standards. The power supply unit of the meter should not be affected in case the maximum voltage of the system appears to the terminals due to faults or due to wrong connections. It should not also be affected by magnet -SMPS Type.

7.	Electronic Components:

The active & passive components should be of the surface mount type are to be handled & soldered by the state of art assembly processes.

USA	 	:	National Semiconductors,Atmel, Philips, Texas

Instruments, BC Component,Fairchild.

Japan 		:	Hitachi, Taiyo Yuden, Oki, Toshiba,AVZ or Ricon

Korea		:	Samsung

Japan 		:	Panasonic, Toshiba,Fairchild,PEC,CTR

Germany 	:	Vishay, Epcos & NSC,Yageo

Taiwan		:         Prolific Technology

8.	Mechanical parts:

a)	The internal electrical components should be of electrolytic copper & should be protected from corrosion, rust etc.

b)	The other mechanical components should be protected from rust, corrosion etc. by suitable plating/painting methods.

9.	Battery:

Maintenance free Lithium battery of long life of 10 years. Only non rechargeable battery should be used for RTC as well as display in absence of Power, since the life & Reliability of these are better than the rechargeable batteries.

Makes

USA		:	Maxell,Varta,Tedirun, Sanyo or National

Japan		:	Panasonic,Sony , Mitsubishi,Sanyo

France 		:	Saft

Korea 		:	Tekcell.

10.	RTC & Micro-controller-The accuracy of RTC shall be as per relevant IEC / IS standards.

USA		:	ST, Teridian, Philips, Dallas, Atmel, Motorola, 					Microchip, Texas Instruments, Holtek, IDT, 						Renesas.

Japan		:	NEC or Oki,Epson.

Malaysia	:     	Intersil.

Taiwan	:        Prolific Technology

11.	P.C.B.:

Glass Epoxy, fire resistance grade FR4, with minimum thickness 1.6 mm if 2 layer and 1.2 mm if 4 layer or more.

Japan 		:	Hitachi, Taiyo Yuden, Oki, Toshiba,AVZ or Ricon

Korea		:	Samsung

Japan 		:	Panasonic, Toshiba,Fairchild,PEC,CTR

Germany 	:	Vishay, Epcos & NSC,Yageo

Taiwan		:	Prolific Technology

ANNEXURE -3a

COMMUNICATION PROTOCOL OF THREE PHASE IrDA NETMETERS

( For Consumer Meters)

Master		: Meter Accessing Instrument with IrDA physical layer standard

( CMRI).

Slave			: Energy Meter ( Considered in this document)

“IR Transceiver 	: Should be complaint to the latest IrDA Physical layer standard” 			   i.e., the details is as follows:

Protocol Information:

General :

Master		: Meter Accessing Instrument with IrDA physical layer standard ( CMRI/ ISBM).

Slave		: Energy Meter

Consumer (Meter) to grid Export parameters

Grid to Consumer (meter) Import parameters

Technical Details

Peak wavelength		: 850-900 nM

Half Angle			: 15o  Minimum cone

Link Distance			: 1.5 m from the top of meter cover

Speed 				: 2.4 kbit/s – 115.2  kbit/s( SIR)

Modulation			: Baseband, no carrier

Window			: Infrared window

Emitter:

Intensity in angular range	: 40- 500 mW /Sr

Rise and Fall time		: 600n Sec Maximum

Receiver:

Irradiance			: 4-5x10 5   µ W/ Cm2

Latency			: 10 m Sec

Communication protocol:

Baud Rate			:  9.6 kbps

Physical layer, SIR,	1/16 at 9.6 kbps

I.Steps for getting data from Meter to CMRI

The following procedure is adopted for getting data from Meter to , through IRPORT.

Format:

- Little Endian

- All values are in Hexadecimal

- Check Sum calculation :

    - if data, then Check Sum = ∑ ~Data,

    - else Check Sum = 0

1a. Command 1 – from CMRI/ISBM to Meter (Initiation Command)

Transmitting Sync packet (11 bytes, Data Nil, with two starting sync bytes) to meters.

| Sync Word | Meter IP | Payload | Command | CMRI/ISBM IP | Data | Checksum |
| --- | --- | --- | --- | --- | --- | --- |
| 16 bit 95h 95h | 24 bit = ffffffh | 8 bit | 8 bit | 24 Bit | Max 242 Bytes | 8 bit |

Example:                                                                        1    2  3  4  5  6   7  8    9  10  11

Transmitting sync packet from CMRI/ISBM to Meter: 95 95 ffff ff  0b 96 31 11 05 00

Sync Word 	= 0x95 0x95

Meter IP 	= All meters in range = 0x 00 00 00  - 0xFF FF FF

Payload 	= 0x0B = 11d

Command 	= 0x96 = 150d

CMRI/ISBM IP 	= 0x31 0x11 0x05 => 0x051131 =   332081d

Check Sum	= 0 (because there is no data)

1b. Response 1 – from Meter to CMRI/ISBM (Initiation Response)

Meters use wireless Collision Avoidance i.e. all meters which receives the  Command 1, gives  response in random time slots of 62.5 ms each up to maximum of 0.5s.

| Sync Word | CMR IP | Payload | Response | Meter IP | Data | Checksum |
| --- | --- | --- | --- | --- | --- | --- |
| 16 bit 95h 95h | 24 bit = ffffffh | 8 bit | 8 bit | 24 Bit | Max 242 Bytes | 8 bit |

Example:0  1    2   3  4   5   6   7   8    9  10   11 12 13 14   15   16 17 18 19

Sequence  : 95 95 31 11 05 14  96 01 1B B7 01 01 1B B7  05  19 00 80 1E 00

| Name | No of Bytes | Byte Posn | Example | Description |
| --- | --- | --- | --- | --- |
|  |  | Offset | Hex Bytes |  |
| Sync Word | 2 | 0,1 | 95 95 | Packet Start identifier |
| Destination ID | 3 | 2,3,4 | 31 11 05 | MRI ID : 0x051131 =332081(Decimal) |
| Pkt Length | 1 | 5 | 0x14 | 20 d |
| Cmd ID | 1 | 6 | 0x96 | 0x96 : Response 1- ID |
| Source ID | 3 | 7,8,9 | 01 1B B7 | Meter ID Eg: 0xB71B01 = 12000001(Decimal) |
| No of packets | 1 | 10 | 0x01 | Single packet |
| Meter ID | 3 | 11,12,13 | 01 1B B7 | Meter ID Eg: 0xB71B01 = 12000001(Decimal) |
| Manufacturing DATE | 1 | 14 | 0x05 | 0x05(BCD Format) - May |
| Version Control ID | 1 | 15 | 0x19 | 18 For Normal meters 19 for Net meters |
| Meter phase | 1 | 16 | 0x00 | 00h:Single Phase ,03h:Three Phase |
| Meter Health Check | 1 | 17 | 0x80 | Meter Status |
| MD Integration Period | 1 | 18 | 0x1E | MD Intergaration Period |
| Check sum | 1 | 19 | 0x00 | Sum of inversion of all the Data Bytes |

2a. Command 2 - from CMRI/ISBM to Meter (Data Command -1) for (Import Parameters)

The CMRI/ISBM will send below command(s) to particular meter which is responded at first.

| Sync Word | Meter IP | Payload | Command | CMRI/ISBM IP | Data | Checksum |
| --- | --- | --- | --- | --- | --- | --- |
| 16 bit 95h 95h | 24 bit | 8 bit | 8 bit | 24 Bit | Max 242 Bytes | 8 bit |

Example:

CMRI/ISBM Command set for packet 1:  95 95 01 1B B7 0B 00 31 11 05 00

Sync Word 		= 95h 95h

Meter Serial Number = Meter IP = 0x011BB7 => 0xB71B01 =  12000001d

Payload 		= 0x 0B = 11d

Command 		= 00 (Command for first packet) / Billing Data

CMRI/ISBM IP 	            = 0x31 0x11 0x05 => 0x051131 =   332081d

Check Sum 	            = 00

2b. Response 2 - from Meter to CMRI/ISBM (Billing data only) (Import Parameters)

Meter will give the billing data as bellow,

| Sync Word | CMR IP | Payload | Response | Meter IP | Data | Checksum |
| --- | --- | --- | --- | --- | --- | --- |
| 16 bit 95h 95h | 24 bit | 8 bit | 8 bit | 24 Bit | Max 242 Bytes | 8 bit |

In detail explanation of Packet 1 of Response 2

| Name | No of Bytes | Byte Posn | Example | Description |
| --- | --- | --- | --- | --- |
|  |  | Offset | Hex Bytes |  |
| Sync Word | 2 | 0,1 | 95 95 | Packet Start identifier |
| Destination ID | 3 | 2,3,4 | 31 11 05 | MRI ID : 0x051131 =332081(Decimal) |
| Pkt Length | 1 | 5 | 0x00 - 0xF8 | 248 bytes |
| Cmd ID | 1 | 6 | 0x00 - 0xFF | 00h : Billing Data |
| Source ID | 3 | 7,8,9 | 01 1B B7 | Meter ID Eg: 0xB71B01 = 12000001(Decimal) |
| RTC– Time | 3 | 10,11,12 | 00 00 00 | hh:mm:ss (24 Hours format) |
| RTC– Date | 3 | 13,14,15 | 00 00 00 | DD:MM:YY |
| Instantaneous Voltage R | 2 | 16,17 | 00 00 | Least count 0.1 (240.1 volts) |
| Instantaneous Voltage Y | 2 | 18,19 | 00 00 | Least count 0.1 (240.1 volts) |
| Instantaneous Voltage B | 2 | 20,21 | 00 00 | Least count 0.1 (240.1 volts) |
| Instantaneous Current R | 2 | 22,23 | 00 00 | Least count 0.01 (12.89 amps) |
| Instantaneous Current Y | 2 | 24,25 | 00 00 | Least count 0.01(12.89 amps) |
| Instantaneous Current B | 2 | 26,27 | 00 00 | Least count 0.01 (12.89 amps) |
| Cum. kWh | 4 | 32 - 35 | 00 00 00 00 | Least count 0.01 |
| Cum. kVAh | 4 | 44 - 47 | 00 00 00 00 | Least count 0.01 |
| LBP1kvAMD | 2 | 48,49 | 00 00 | Least count 0.01 |
| MD Time | 2 | 50,51 | 00 00 | HH:mm (24hr format) |
| MD Date | 3 | 52,53,54 | 00 00 00 | DD:MM:YY |
| Make Code | 3 | 55,56,57 | 00 00 00 | XXX (TEXT format) |
| Phase | 1 | 58 | 0x03 | 00h:Single Phase ,03h:Three Phase |
| Meter Multiplying factor | 2 | 59,60 | 0001 | XXXX (Fixed value 1) |
| MD Reset Count | 2 | 77,78 | 00 00 | 00 - 65535 |

2c. Command 2 - from CMRI/ISBM to Meter (Data Command -1) for (Export Parameters)

The CMRI/ISBM will send below command(s) to particular meter which is responded at first.

| Sync Word | Meter IP | Payload | Command | CMRI/ISBM IP | Data | Checksum |
| --- | --- | --- | --- | --- | --- | --- |
| 16 bit 95h 95h | 24 bit | 8 bit | 8 bit | 24 Bit | Max 242 Bytes | 8 bit |

Example:

CMRI/ISBM Command set for packet 1:  95 95 01 1B B7 0B 00 31 11 05 00

Sync Word 		= 95h 95h

Meter Serial Number = Meter IP = 0x011BB7 => 0xB71B01 =  12000001d

Payload 		= 0x 0B = 11d

Command 		= 01 (Command for second packet) / Billing Data

CMRI/ISBM IP 	            = 0x31 0x11 0x05 => 0x051131 =   332081d

Check Sum 	            = 00

2d. Response 2 - from Meter to CMRI/ISBM (Billing data only) (Export Parameters)

Meter will give the billing data as bellow,

| Sync Word | CMR IP | Payload | Response | Meter IP | Data | Checksum |
| --- | --- | --- | --- | --- | --- | --- |
| 16 bit 95h 95h | 24 bit | 8 bit | 8 bit | 24 Bit | Max 242 Bytes | 8 bit |

In detail explanation of Packet 2 of Response 2b

| Name | No of Bytes | Byte Posn | Example | Description |
| --- | --- | --- | --- | --- |
|  |  | Offset | Hex Bytes |  |
| Sync Word | 2 | 0,1 | 95 95 | Packet Start identifier |
| Destination ID | 3 | 2,3,4 | 31 11 05 | MRI ID : 0x051131 =332081(Decimal) |
| Pkt Length | 1 | 5 | 0x00 - 0xF8 | 248 bytes |
| Cmd ID | 1 | 6 | 0x00 - 0xFF | 00h : Billing Data |
| Source ID | 3 | 7,8,9 | 01 1B B7 | Meter ID Eg: 0xB71B01 = 12000001(Decimal) |
| RTC– Time | 3 | 10,11,12 | 00 00 00 | hh:mm:ss (24 Hours format) |
| RTC– Date | 3 | 13,14,15 | 00 00 00 | DD:MM:YY |
| Instantaneous Voltage R | 2 | 16,17 | 00 00 | Least count 0.1 (240.1 volts) |
| Instantaneous Voltage Y | 2 | 18,19 | 00 00 | Least count 0.1 (240.1 volts) |
| Instantaneous Voltage B | 2 | 20,21 | 00 00 | Least count 0.1 (240.1 volts) |
| Instantaneous Current R | 2 | 22,23 | 00 00 | Least count 0.01 (12.89 amps) |
| Instantaneous Current Y | 2 | 24,25 | 00 00 | Least count 0.01(12.89 amps) |
| Instantaneous Current B | 2 | 26,27 | 00 00 | Least count 0.01 (12.89 amps) |
| Cum. kWh | 4 | 32 - 35 | 00 00 00 00 | Least count 0.01 |
| Cum. kVAh | 4 | 44 - 47 | 00 00 00 00 | Least count 0.01 |
| LBP1kvA MD | 2 | 48,49 | 00 00 | Least count 0.01 |
| MD Time | 2 | 50,51 | 00 00 | HH:mm (24hr format) |
| MD Date | 3 | 52,53,54 | 00 00 00 | DD:MM:YY |
| Make Code | 3 | 55,56,57 | 00 00 00 | XXX (TEXT format) |
| Phase | 1 | 58 | 0x03 | 00h:Single Phase ,03h:Three Phase |
| Meter Multiplying factor | 2 | 59,60 | 0001 | XXXX (Fixed value 1) |
| MD Reset Count | 2 | 77,78 | 00 00 | 00 - 65535 |

3. Command 3 – from CMRI/ISBM to Meter (Closing Command)

CMRI/ISBM will send the below command to the meter to stop / close the communication

| Sync Word | Meter IP | Payload | Command | CMRI/ISBM IP | Data | Checksum |
| --- | --- | --- | --- | --- | --- | --- |
| 16 bit 95h 95h | 24 bit = ffffffh | 8 bit | 8 bit | 24 Bit | Max 242 Bytes | 8 bit |

Example:

CMRI/ISBM Command set for Closing command :95 95 01 1B B7 0B 9e 31 11 05 00

Sync Word 		= 95h 95h

Meter Serial Number = Meter IP = 0x011BB7 = 12000001d

Payload 		= 0x 0B = 11d

Command 		= 0x9e = 158d

CMRI/ISBM IP          = 0x31 0x11 0x05 => 0x051131 =   332081d

Checksum		= 0x00

* After receiving closing command from CMRI / ISBM, the meter should not respond to broadcast command till 15 minutes.

*	Meter has to display “DONE”  in case of billing data

Data is then downloaded for each valid meter in sequence.

The CMRI restarts the process 3 times till no meter response is found.

NOTE

The participating bidders shall give demonstration  of their meters for data downloading and generation of spot bills through ISBMs within one month from the date of opening of the technical bid.

### SECTION - VII

### SAMPLE FORMS

1.  BID FORM

Date.  .......

TO: (Name and Address of Purchaser)

Gentlemen and/or Ladies:

Having examined the Bidding documents, the receipt of which is hereby duly acknowledged, we, the undersigned, offer to supply and deliver.  ......................... (Description of Materials / equipment) in conformity with the said bidding documents in accordance with the prices quoted online and made part of this Bid.

We undertake, if our Bid is accepted, to deliver the Materials / equipment in accordance with the delivery schedule specified in the Schedule of Requirements.

If our Bid is accepted, we will obtain the guarantee of a bank in a sum equivalent to. 10% of the Contract Price for the due performance of the Contract, in the form prescribed by the Purchaser.

We agree to abide by this Bid up to ……………. (For the Bid Validity Period) specified in Clause and it will remain binding upon us and may be accepted at any time before the expiration of that period.

Until a formal contract is prepared and executed, this Bid, together with your written acceptance thereof and your notification of award, will constitute a binding Contract between us.

We understand that you are not bound to accept the lowest or any bid you may receive.

We certify / confirm that we comply with the eligibility requirements as per  clause  of the bidding documents.

Dated this.  ...........day of.  .............200

____________________________

____________________________

[Signature] 					[in the capacity of]

Duly authorized to sign Bid for and on behalf of _____________________________

2. (a) BID SECURITY FORM

Whereas.  .............. (hereinafter called "the Bidder") has submitted its Bid dated (date of submission of bid) for the supply of.  ....................(name and /or description of the Materials / equipment) (hereinafter called "the Bid").

KNOW ALL PEOPLE by these presents that WE.  .............(name of bank) having our registered office at.  ...........(address of bank)(hereinafter called "the Bank"), are bound unto.  ...............(name of Purchaser) (hereinafter called "the Purchaser") in the sum of                   for which payment well and truly to be made to the said Purchaser, the Bank binds itself, its successors, and assigns by these presents. Sealed with the Common Seal of the said Bank this          day of             200  .

THE CONDITIONS of this obligation are:

1.	If the Bidder

a) 	withdraws its Bid during the period of bid validity specified by the Bidder on the Bid Form; or

- does not accept the correction of errors in accordance with the Bid Specification, or

2.	If the Bidder, having been notified of the acceptance of its bid by the Purchaser during the period of bid validity;

(a)	fails or refuses to furnish the performance security, in accordance with the Bid Specification.

(b)	fails or refuses to execute the Contract Form if required; or

We undertake to pay the Purchaser up to the above amount upon receipt of its first written demand, without the Purchaser having to substantiate its demand, provided that in its demand the Purchaser will note that the amount claimed by it is due to it, owing to the occurrence of one or both of the two conditions, specifying the occurred condition or conditions.

This guarantee will remain in force up to and including forty five (45) days after …………….(Specification Date) the period of the bid validity, and any demand in respect thereof should reach the Bank not later than the above date.

.  ....................

(Signature of the Bank)

NOTE:	This will be executed on a Rs.100/- non-judicial stamp paper issued by a scheduled Bank.

2(b) PERFORMANCE SECURITY FORM

To:                        (Name of Purchaser)

WHEREAS………………………………………..(Name of Supplier)

(hereinafter called "the Supplier") has undertaken, in pursuance of Contract No.............dated.............200 to supply.  ................(Description of Materials / equipment and Services)

(hereinafter called "the Contract").

AND WHEREAS it has been stipulated by you in the said Contract that the Supplier will furnish you with a Bank Guarantee by a recognized Bank for the sum specified therein as security for compliance with the Supplier's performance obligations in accordance with the Contract.

AND WHEREAS we have agreed to give the Supplier a Guarantee:

THEREFORE WE hereby affirm that we are Guarantors and responsible to you, on behalf of the Supplier, up to a total of.  ............................ (Amount of the Guarantee in Words and Figures) and we undertake to pay you,  upon your first written demand declaring the Supplier to be in default under the Contract and without cavil or argument, any sum or sums within the limit of................ (Amount of Guarantee) as aforesaid, without your needing to prove or to show grounds or reasons for your demand or the sum specified therein.

This guarantee is valid until the.  ... day of.  ..... 200.

Signature and Seal of Guarantors

..........................................

Date.  .......................200.

..........................................

..........................................

Address:....................…...

..........................................

..........................................

NOTE:	This will be executed on a Rs.100/- non-judicial stamp paper by a scheduled Bank.

3. CONTRACT FORM

THIS AGREEMENT made the.  ....... day of.  ............ 200  Between.  ..............(Name of Purchaser) of the one part and.  ..........(Name of Supplier) of the other part:

WHEREAS   the Purchaser invited bids for certain Materials / equipment and ancillary services viz.,

.....................(Brief description of Materials / equipment and Services) and has accepted a bid by the Supplier for the supply of those Materials / equipment and services in the sum of.  .....................(Contract Price in Words and Figures)(hereinafter called "the Contract Price").

NOW THIS AGREEMENT WITNESSETH AS FOLLOWS:

1.	In this Agreement words and expressions will have the same meanings as are respectively assigned to them in the Conditions of Contract referred to.

2.	The following documents will be deemed to form and be read and construed as part of this Agreement, viz.:

(a)	the Bid Form and the Price Schedule submitted by the  Bidder;

(b)	the Schedule of Requirements;

(c)	the Technical Specifications;

(d)	the General Conditions of Contract;

(e)	the Purchaser's Notification of Award.

3.	In consideration of the payments to be made by the Purchaser to the Supplier as hereinafter mentioned, the Supplier hereby covenants with the Purchaser to provide the Materials / equipment and services and to remedy defects therein in conformity in all respects with the provisions of the Contract.

4.	The Purchaser hereby covenants to pay the Supplier in consideration of the provision of the Materials / equipment and services and the remedying of defects therein, the Contract Price or such other sum as may become payable under the provisions of the Contract at the times and in the manner prescribed by the Contract.

Brief particulars of the Materials / equipment and services which will be supplied/ provided by the Supplier are as under:

| Sl. No. | Brief Description of Materials / Equipment & services | Quantity to be supplied | Unit Price Rs. | Total Price Rs. | Delivery Terms |
| --- | --- | --- | --- | --- | --- |

TOTAL VALUE:	(Rupees 			     	 		only)

DELIVERY SCHEDULE:

IN WITNESS whereof the parties hereto have caused this Agreement to be executed on the day and year first above written.

Signed, Sealed and Delivered by the

said.  ..............................(for the Purchaser)

in the presence of.  ................

Signed, Sealed and Delivered by the

said.  ..............................(for the Supplier)

in the presence of.  ................

NOTE:	To be executed on a Rs.100/- Non-judicial stamp paper.

4.  PROFORMA FOR PERFORMANCE STATEMENT

Bid No.__________				Date of Opening________

Time _______ Hours

Name of the Firm__________________________________________

| Order placed by (full address of purchaser) | Order No. and Date | Description and quantity of ordered equipment | Date of Completion of Delivery |  |
| --- | --- | --- | --- | --- |
|  |  |  | As per Contract | Actual |

| Remarks indicating reasons for late delivery, if any | Has the equipment been satisfactorily functioning? (Attach a Certificate from the Purchaser) |
| --- | --- |

Signature of the Bidder _______________________

________________________

________________________

(FORMAT-A)

5. DETAILS TO BE FURNISHED BY THE MANUFACTURER

| 1. Specification No. | : |  |
| --- | --- | --- |
| 2. Name of the Material | : |  |
| 3. Quantity to be procured | : |  |
| 4. Last date and time for submission of Bid | : |  |
| 5. Date and time for opening of Bid | : |  |
| 6. State whether Bid guarantee is enclosed | : |  |
| 7. State whether the quotation in two parts has been submitted. | : |  |
| 8. State whether 20% minimum quantity is quoted | : |  |
| 9. Whether willing to furnish performance B.G. @ 10% if order is placed | : |  |
| 10. Whether month wise delivery schedule indicated | : |  |
| 11. Prices whether Firm | : |  |
| 12. Whether any other tax / duty payable. If so give details and the same is included / not included. | : |  |
| 13. State whether TSSPDCL(erstwhile TSSPDCL) terms of payment are accepted. | : |  |
| 14. Quantity offered for supply | : |  |
| 15. State whether 90 days validity offered | : |  |
| 16. Whether sample is enclosed (if specified) | : |  |
| 17. Whether the material / equipment offered conforms to the relevant TSSPDCL(erstwhile TSSPDCL) Specification | : |  |
| 18. Whether you have executed orders of the TSSPDCL(erstwhile TSSPDCL) previously for these items. (Please give details) | : |  |
| 19. Similar details in respect of supplies made to other utilities | : |  |
| 20. Whether Bid guarantee exemption letter enclosed, if exempted. | : |  |
| 21. Whether sales tax clearance certificate enclosed | : |  |
| 22. Whether Income-tax clearance certificate enclosed. | : |  |
| 23. Whether Warranty clause accepted | : |  |
| 24. Whether Penalty clause accepted | : |  |
| 25. Whether delivery schedule accepted | : |  |

6. SCHEDULE OF DEVIATION

# (i) TECHNICAL

| Sl. No. | Requirements / Equipment | Specification Clause No. | Deviations | Remarks |
| --- | --- | --- | --- | --- |

It is hereby conformed that except for deviations mentioned above, the offer conforms to all the other features specified in Technical Specification Section ____ of this Bid Document

Place :								Signature of the Bidder :

Date :								Name :

Business address  :

6. SCHEDULE OF DEVIATION

# (ii) COMMERCIAL

| Sl. No. | Requirements / Equipment | Specification Clause No. | Deviations | Remarks |
| --- | --- | --- | --- | --- |

It is hereby conformed that except for deviations mentioned above, the offer conforms to all the other features specified in Commercial Specification Section ____ of this Bid Document

Place :								Signature of the Bidder :

Date :								Name :

Business address:

r

Designation

Date:

7. DECLARATION FORM

Declaration to be given by the Company in regard to relation to promoters of Blacklisted / debarred companies by any power utilities.

I declare that, myself or any of the representatives of my company / firm do not have any relatives with promoters of blacklisted / debarred companies by any utilities.

It is certified that the information furnished above is true to the best of my knowledge and belief. It is hereby undertaken that in the event of the above information found to be false or incorrect at a later date, the TSSPDCL is entitled to terminate the contract/agreement entered into besides recovering damages as may be found necessary, with due notice.

Signature of authorized representative