TENDER SPECIFICATION

STN-1176/24-25

FOR

### 11KV 200A (TT) GOAB SWITCHES WITH POST TYPE POLYMER INSULATORS

(Tender QUANTITY: 10,000 Nos.)

TABLE OF CONTENTS

SECTION	DESCRIPTION			    		      	 	        PAGE NO.

I		Notice inviting bids							4-6

II		Salient Features of the Bid			  			7

III		General Terms and Conditions of Contract					8 to 33

IV		Schedule of Materials							34

V		Technical Specification							35-55

VI	   	Qualification Requirements        		           				56

VII		Sample Forms								57

1)	Bid Form		                    					58

2)          Bid Security Form                                                         				59

3)	Performance Security Form				      		60

4)	Contract Form								61-62

5)	Details to be furnished by the Manufacturer                                               	63

6)	Performance Statement							64

7)            Schedule of Deviations (Technical & Commercial)  				65

8) 	Declaration to be given by the company in regard to relation to

promoters of blacklisted / debarred companies by any power utilities	 	66

NOTE:

- Payment terms, Delivery period, Performance Bank Guarantee, applicable GST” should be in line with the terms and conditions of the specification. If any bidder does not meet any one of the conditions, such tender will not be considered. Please note that the conditional offers are also not considered. Hence the bidder shall submit the tender in line with the terms and conditions of the specification.

2.	The bidders shall check the website www.tssouthernpower.com and www.tender.telangana.gov.in for amendments, if any, upto one day prior to the date of tender opening. The amendments shall be binding on the bidders.

3.	The purchaser will not be responsible for any damage that may be caused to the samples at any time.

4.	The bidder shall furnish required Bid Security amount and validity as per specification.  If the bidder fails to furnish bid security amount and bid validity as stipulated in the specification, such tender bid will not be considered for further evaluation.

5.	The prospective bidders shall attend the pre-bid meeting (date and time in NIT) for any queries.  The discussed queries shall be submitted in the form of a letter during pre bid meeting or within 24 hrs of pre bid meeting.  Any new queries received after pre bid meeting are not liable to be considered.

6.	The bid evaluation will be carried out based on the documents uploaded through www.tender.telangana.gov.in against this tender.

7. 	The Bids received with any details revealing the prices in the Online PQ stage/offline Technical bid or any other mode other than in online commercial bid will be liable for rejected.

8.	In e-procurement commercial stage, if F&I charges are applicable then the firm must mention the F&I charges entered are exclusive/inclusive of GST in the remarks section. If not mentioned in remarks F&I charges will be considered as inclusive of GST.

11. 	EMD Exemption is considered Only for Government firms.

12.	Applicable tax collected at source (TCS) is as per Government of India.

Ph : 040 – 23431026, 1035

-SD/-

CHIEF GENERAL MANAGER (P&MM)

TGSPDCL

SECTION- I

| Energy Saved is |  | SOUTHERN POWER DISTRIBUTION COMPANY OF TELANGANA LTD. |
| --- | --- | --- |
|  | Energy Produced |  |

# e-Procurement Tender Notice (Paper Notification)

TSSPDCL intends to float tenders for procurement of (a) LT Distribution Boxes (SMC) (b) 11KV 3-Ph 500 KVA Copper Wound DTR (Star-2) (c)11KV CTPT Sets, (d)11KV & 33KV CTs and 11KV PTs, 0.2 class (d) Various sizes of cables (e) 8 Mtrs and 9.1 Mtrs Poles, (f)12 V & 24 V 40AH Batteries and Battery charges, (g) 11KV 200A TT AB Switches, (h)Stationery items, (i) Hiring of Multifunctional machines, (j) Catering service in CPTI, Hyd., (k)LT Pin Insulators (l) 11KV & 33KV feeder VCBs and (m) Auction for scrap materials on e-procurement platform and e-auction platform.

For further details of each item above, please visitwww.tssouthernpower.com, www.tender.telangana.gov.in and www.auction.telangana.gov.in.

Phone: 040-23431360, 1033, 1035, 1026

(U.BALASWAMY)

CHIEF GENERAL MANAGER (P&MM)

ONLINE VERSION

Tender Notice No: STN-1176/24-25

| Notice Inviting Tender Details |  |  |
| --- | --- | --- |
| S.No | Description |  |
| 1 | Department Name | TGSPDCL |
| 2 | Office | Purchases & Material Management Wing, Corporate Office, TGSPDCL. |
| 3 | Tender Number | STN-1176/24-25 |
| 4 | Tender Subject and Quantity (Nos.) | 11KV 200A (TT) GOAB SWITCHES WITH POST TYPE POLYMER INSULATORS :10,000 Nos.. |
| 5 | Delivery Schedule | The delivery of materials shall commence within 45 days from the date of receipt of purchase order and complete three (3) months thereafter. The rate of monthly delivery may be quoted. The rate of monthly delivery may be quoted. |
| 6 | Tender Type | Open |
| 7 | Tender Category | NA |
| 8 | Bid Security (INR) | (i) The bidder shall furnish, as part of its bid, a Bid security in the amount of 2.36% of the Total Ex-works value of the materials offered against the bid or the amount specified by the Purchaser or part quantity may furnish proportionate bid security (or) (ii) Exemption letter of Bid Security in case of Govt. firms. |
| 9 | Bid Security Payable to | In the form of, - DD in favour of Pay Officer/TGSPDCL/Hyd Or - BG in favour of CGM/P&MM/CO/ TGSPDCL/HYD from Nationalized/Scheduled bank as per format-II whose validity should not be less than 135 days from the date of opening of tender. Or Online by utilizing the payment Gateway Service on E-procurement platform. |
| 10 | Processing Fee (INR) | NIL |
| 11 | Transaction Fee | Transaction fee: All the participating bidders who submit the bids have to pay an amount @ 0.03% of their final bid value online with a cap of Rs. 10,000/- for quoted value of purchase upto Rs.50 crores and Rs.25,000/- if the purchase value is above Rs.50 crores & GST applicable as levied by Govt. of India on transaction fee through online in favour of TSTS. The amount payable to TSTS is non refundable. Corpus Fund: Successful bidder has to pay an amount of 0.04% on quoted value through demand draft in favour of Managing Director, TSTS, Hyderabad towards corpus fund at the time of concluding agreement. |
| 12 | Transaction Fee Payable to | M/s. TSTS, Hyderabad |
| 13 | Date & time of pre-bid meeting with manufacturers | 24-05-2024 at 11.30 Hrs. |
| 14 | Schedule Sale opening date | 20-05-2024 from 17:00 Hrs. |
| 15 | Schedule Sale closing Date | 04-06-2024 Upto 12:00 Hrs. |
| 16 | Bid Submission Closing Date & time | 04-06-2024 Upto 12:00 Hrs. |
| 17 | Bid submission | On Line |
| 18 | Pre-Qualification& Technical Bid Opening Date (Qualification and Eligibility Stage and Technical Bid Stage) | 04-06-2024 at 15:00 Hrs. |
| 19 | Price Bid Opening Date (Financial Bid Stage) | 05-06-2024 at 12:00 Hrs. |

| 20 | Place of Tender Opening | O/o Chief General Manager/P&MMTGSPDCL, 4th Floor, Corporate Office, Mint Compound, Hyderabad – 500 004. |
| --- | --- | --- |
| 21 | Officer Inviting Bids/ Contact Person | Chief General Manager/P&MM/TGSPDCL/HYDERABAD |
|  | Address/E-mail id | O/o. Chief General Manager/P&MM, TGSPDCL, 4th Floor, Corporate Office, Mint Compound, Hyderabad – 500 004, cgmpmm@tssouthernpower.com |
| 22 | Contact Details/Telephone, Fax | Ph. No. 040-23431319, 23431026 |
| 23 | Eligibility Criteria | As per Section IV |
| 24 | Procedure for Bid Submission | Bids shall be submitted online on www.tender.telangana.gov.in platform - The participating bidders in the tender should register themselves free of cost on e-procurement platform in the website www.tender.telangana.gov.in. - Bidders can log-in to e-procurement platform in Secure mode only by signing with the Digital certificates. - The bidders who are desirous of participating in e-procurement shall submit their technical bids, price bids as per the standard formats available at the e-market place. - The bidders should scan and upload the following documents in support of technical bids. The bidders shall sign on all the statements, documents certificates uploaded by him, owning responsibility for their correctness/authenticity: a) Bid Security should be furnished in the form of DD in favour of Pay Officer/TGSPDCL/Hyd Or BG in favour of CGM/P&MM/CO/TGSPDCL/HYD whose validity should not be less than 135 days from the date of opening of tender Or Online by utilizing the payment Gateway Service on E-procurement platform Exemption in case of Govt. firms (As per clause 19.40) b) “GSTR 3B returns” For last FY c) Financial Turnover certified by CA for 5 years d) Details of previous supplies along with purchase order and delivery challan copies for 40% qualification requirement as per tender document. e) Performance certificates from purchaser of utilities for 20% qualification requirement as per tender f) Copies of previous supply orders and relevant purchase order copies mentioned in the performance certificates in support of the above. g) Drawings, Guaranteed Technical Particulars of the product, other relevant documents attached to the bid. h) Type test certificates (CPRI/ERDA or any NABL accredited Lab) i) Duly filled and signed proforma as per Format 5. j) Transaction fee payable to TSTS k) Proof of manufacturer, valid certificates of MSMED certificates, NSIC certificates etc., 5. The rates should be quoted in online only |
| 25 |  | 6. The bidders should upload the documents in PDF format only .After uploading the documents the copies of the uploaded statement, certificates, documents, original Demand Drafts or BG in respect of Bid Security (except the Price bid/offer/break-up of GST) are to be submitted by the bidder to the Chief General Manager/P&MM/TGSPDCL so as to reach before the date and time of opening of the technical bid. Failure to furnish any of the uploaded documents, certificates, before the date and time of opening of technical bid will entail in rejection of the bid. The Department shall not hold any risk on account of postal delay. Similarly, if any of the certificates, documents, etc., furnished by the tenderer are found to be false/fabricated/bogus, the bidder will be disqualified, blacklisted, action will be initiated as deemed fit and the Bid Security will be forfeited. 7. The department will not hold any risk and responsibility regulating non-visibility of the scanned and uploaded documents. 8. The Documents that are uploaded online on e-market place will only be considered for Technical Bid Evaluation. 9. Important Notice to Contractors, Suppliers and Department users (i) In the endeavor to bring total automation of processes in e-Procurement, the Govt. has issued orders vide G.O.Ms.No. 13 dated. 5.7.2006 permitting integration of electronic Payment Gateway of ICICI/HDFC Banks with e-Procurement platform, which provides a facility to participating suppliers/ contractors to electronically pay the transaction fee online using their credit cards. |
| 26 | Rights reserved with the Department | TGSPDCL reserves the right to accept or reject any or all of the tenders received without assigning any reasons therefore. The TGSPDCL also reserves the right to split the tender and place orders on more than one tenderer at its discretion. |
| 27 | General Terms and Conditions | As per tender documents. |

SECTION-II

SALIENT FEATURES OF THE BID

Superscription on the Tender Cover

Specification No				: STN-1176/24-25

Material			: 11KV 200A (TT) GOAB SWITCHES WITH POST TYPE POLYMER 		INSULATORS

Officer to whom the bid will be addressed	: CGM/P&MM/TGSPDCL/Hyderabad.

Superscription on the bid cover and

the outer envelope

- Specification No.  			      	 : STN-1176/24-25

- Due date and time for online submission 	: 04-06-2024 upto 12.00 Hrs.

- Date and time of online opening             	: 04-06-2024 at 15: 00 Hrs

- Payment of bid security

i) If paid give details: DD No./BG.No._____Dt.___ for Rs.______

ii) If exempted give details in case of Government organization.

e. Whether 90 days validity offered ………(yes/no).

f. Whether bid is made accepting payment terms Clause….(yes/no).

g. Whether delivery is as per delivery schedule indicated….(yes/no)

h. Whether the quotation is in two parts …. (Yes/no)

Content of Bidding Documents:

The materials / equipment required, bidding procedures, and contract terms are prescribed in the bidding documents as listed below:

        - Notice Inviting Bids.

        - Salient features of the contract.

        - Standard General terms and conditions of contract.

        - Standard Technical specification and drawings wherever necessary.

        - Qualification Requirements.

        - Schedule of requirements (Delivery Schedule)

SAMPLE FORMS.

        - Bid Form and Price Schedules

        - Bid Security Form

          - Contract Form

          - Performance Security form

i.		Manufacturers’ Authorization form

j. 	Performance Statement

k.	Details to be furnished by the Manufacturer

l.	Schedule of Deviations (Technical & Commercial)

The Bidder is expected to examine all instructions, forms, terms and technical specifications in the bidding documents. Failure to furnish all information required by the bidding documents or to submit a bid not substantially responsive to the bidding documents in every respect will be at Bidder's risk and may result in the rejection of its bid.

Deviations from standard bidding document

i.	General terms and Conditions of Contract

ii	Technical

The above deviations supercede the existing terms of GCC and Technical Specification

-SD/-

Chief general manager (P&MM)

TGSPDCL

GENERAL TERMS AND CONDITIONS OF CONTRACT

Table of Clauses

| A | Introduction | 10 |
| --- | --- | --- |
| 1 | Definitions | 10 |
| 2 | Applicability | 10 |
| 3 | (a) Standards | 10 |
| 3 | (b) Interchangeability | 10 |
| 4 | Scope of Work | 10 |
| 5 | Eligible Bidders | 11 |
| B | The Bidding Documents | 11 |
| 6 | Contents of Bidding Document | 11 |
| 7 | Clarification of Bidding Documents | 11 |
| 8 | Amendment to Bidding Documents | 11 |
| C | Preparation of Bids | 12 |
| 9 | Language of the Bid | 12 |
| 10 | Cost Associated with Bidding | 12 |
| 11 | Documents Constituting the Bid | 12 |
| 12 | Bid Form | 12 |
| 13 | Bid Prices | 12 & 13 |
| 14 | Taxes | 13 |
| 15 | Statutory Variations | 13 |
| 16 | Bid Currencies | 13 |
| 17 | Quantity to quote | 13 |
| 18 | Documents Establishing Bidders Eligibility and Qualifications | 14 |
| 19 | Bid Security | 14-15 |
| 20 | Period of Validity of Bids | 16 |
| 21 | GSTR 3B returns | 16 |
| 22 | Service Condition | 16 |
| 23 | Format and Signing of Bids | 16 |
| D | Submission of Bids | 17 |
| 24 | Sealing and Marking of Bids | 18 |
| 25 | Deadline for Submission of Bids | 18 |
| 26 | Late Bids | 18 |
| E | Opening and Evaluation of Bids | 19 |
| 29 | Opening of Bids by the Purchaser | 19 |
| 28 | Clarification of Bids | 19 |
| 29 | Preliminary Examination | 19 |
| 30 | Evaluation and Comparison of Bids | 20-22 |
| 31 | Contacting the Purchaser | 22 |
| F | Award of Contract | 22 |
| 32 | Post Qualification | 22 |
| 33 | Award Criteria | 22-23 |
| 34 | Purchaser's Right to Vary Quantities at Time of Award | 23 |
| 35 | Purchaser's Right to accept any Bid& to reject any or all bids | 23 |
| 36 | Notification of Award | 23 |
| 37 | Signing of Contract | 23 |
| 38 | Performance Security | 24 |
| 39 | Corrupt or Fraudulent Practices | 24 |
| 40 | Use of Contract Documents and Information | 25 |
| 41 | Patent Rights | 25 |
| 42 | Places / Locations | 25 |

| 43 | Delivery | 25 |
| --- | --- | --- |
| 44 | Inspection and Tests | 26 |
| 45 | Name Plate | 26 |
| 46 | Packing | 27 |
| 47 | Delivery Documents | 27 |
| 48 | Insurance | 27-28 |
| 49 | Transportation | 28 |
| 50 | Incidental Services | 28 |
| 51 | Spare Parts | 28 |
| 52 | Warranty | 29 |
| 53 | Payment | 29-30 |
| 54 | Prices | 30 |
| 55 | Change Orders | 30 |
| 56 | Contract Amendments | 30 |
| 57 | Assignment | 30 |
| 58 | Delays in Supplier’s Performance | 31 |
| 59 | Penalty for delay in supplies | 31 |
| 60 | Risk Purchase | 31 |
| 61 | Termination for Default | 32 |
| 62 | Termination for Insolvency | 32 |
| 63 | Termination for Convenience | 32 |
| 64 | Force Majeure | 32 |
| 65 | Settlement of Disputes | 33 |
| 66 | Jurisdiction | 34 |
| 67 | Notices | 34 |
| 68 | Foreign Exchanges | 34 |

SECTION-III

GENERAL TERMS AND CONDITIONS

A. Introduction

- Definitions

1.1	In this Contract, the following terms will be interpreted as indicated:

- "The Contract" means the agreement entered into between the Purchaser and the Supplier, as recorded in the contract Form signed by the Parties, including all attachments and appendices thereto and all documents incorporated by reference therein.

- "The Contract Price" means the price payable to the Supplier under the Contract for the full and proper performance of its contractual obligations.

(c)	"The Materials/equipment" means all of the equipment, machinery, and/or other materials which the Supplier is required to supply to the Purchaser under the Contract.

(d)	"The Services" means those services ancillary to the supply of the Materials / equipment, such as transportation and insurance, and any other incidental Services, such as installation, commissioning, provision of technical assistance, training, and other such obligations of the Supplier covered under the Contract.

(e)	"GCC" means the General Terms and Conditions of Contract contained in the section.

(f)	"The Purchaser" means the organization purchasing the Materials / equipment.

(g)	Vendor is a supplier who has registered with the purchaser for supply of materials/equipment.

(h)	"The Supplier" means the firm supplying the Materials / equipment and Services under this Contract.

(i)	"Day" means calendar day.

2.	Applicability

  - These General Conditions of contract will apply to the extent that they are not superseded by provisions of Salient features of the Bid.

3(a)	Standards

The Materials / equipment supplied under this Contract will conform to the Standards mentioned in the Technical specifications, and, when no applicable standard is mentioned, the authoritative standards appropriate to the Materials / equipment' i.e., BIS, such standards will be the latest. All material will be of the best class and will be capable of satisfactory operation under tropical conditions without distortion or deterioration.

3(b)	Interchangeability:

All similar materials and removable parts of similar equipment will be interchangeable with each other.  A specific confirmation of this should be furnished in the bid.

4. 	Scope of Work:

This specification covers design, manufacture, testing and delivery FADS (Free At Destination Stores) of the materials described at Section IV and Technical Specification at section-V.

5.	Eligible Bidders:

All the Manufacturers who have registered themselves with Department of Industries of State/Central Govt. with full manufacturing and testing facilities for supply of the material / equipment listed in Section No. VII, of Bid specification and meeting the qualification requirements described at section VI only need quote. Bids received from firms not meeting the above two criteria will not be considered.

### B.  THE BIDDING DOCUMENTS

6.	Contents of Bidding Document:

6.1	The Materials / equipment required, bidding procedures, and contract terms are prescribed in the bidding documents as listed below:

- Notice Inviting Bid

- Technical Specifications

- Schedule of Requirements (Delivery Schedule)

- Bid Form and Price Schedules (online only)

- Salient Features of the Bid

- General Terms and Conditions of Contract

- Qualification Requirements

- Bid Security

- Performance Security Form

- Schedule of Deviations

6.2	The Bidder is expected to examine all instructions, forms, terms and Technical specifications in 	the bidding documents. Failure to furnish all information required by the bidding documents 	or 	to submit a bid not responsive to the bidding documents in every respect will be at Bidder's 	risk 	and may result in the rejection of its bid.

7.	Clarification of Bidding Documents

A prospective Bidder requiring any clarification of the bidding documents may notify the 	Purchaser in writing or by cable (hereinafter, the term cable is deemed to include telex and 	facsimile) at the Purchaser's address. The Purchaser will respond in writing to any request for 	clarification of the bidding documents, which it receives no later than fifteen (15) days prior to 	the deadline for the submission of bids. Written copies of Purchaser's response (including an 	explanation of the query but without identifying the source of inquiry) will be put on Website of 	the purchaser or intimated by mail.

8.	Amendment to Bidding Documents:

8.1	At any time prior to the deadline for submission of bids, the Purchaser, for any reason, whether at its own initiative or in response to a clarification requested by a prospective Bidder, may modify the bidding documents by amendment.

8.2	All such amendments also would be made available on the website of TGSPDCL and                      e-procurement website and such amendments will be binding on the respective Bidders.

8.3	In order to allow prospective Bidders reasonable time in which to take the amendment into account in preparing their bids, the Purchaser, at its discretion, may extend the deadline for the submission of bids.

C. PREPARATION OF BIDS

9.	Language of Bid:

The bid prepared by the Bidder including all correspondence and documents relating to the bid exchanged by the Bidder and the Purchaser, will be in English.

10.	Cost Associated with Bidding:

The Bidder will bear all costs associated with the preparation and submission of its bid, and the Purchaser, will in no case be responsible or liable for those costs, regardless of the conduct or outcome of the bidding process.

11.	Documents Constituting the Bid:

11.1	The bid prepared by the Bidder will comprise the following components:

    - Bid Security in accordance with Clause No.19.

    - A Bid Form and Price Schedule (only for online commercial stage submission) completed in accordance with Clause No.12 and 13.

    - Documentary evidence establishing in accordance with Clause No.18 that the Bidder is eligible to bid and is qualified to perform the contract if its bid is accepted.

    - Documentary evidence establishing that the Materials / equipment and ancillary services to be supplied by the Bidder are as per the Technical specification of the bidding documents; and

    - GSTR 3B returns

    - Schedule of Deviations

(a) Commercial

(b) Technical

All the Schedules will be duly filled but not necessary in the sheets attached to the specification unless full details required in the schedules are furnished, the Bids will be liable for rejection.

12.	Bid Form:

12.1	The Bidder will complete the Bid form and the appropriate Price Schedule (only for online commercial stage submission) furnished in the bidding documents, indicating the Materials/ equipment to be supplied, a brief description of the Materials / equipment, quantity and prices.

13. 	Bid Prices:

13.1	The prices quoted shall be FIRM. Bids will be called for with prices separately for Ex-works value for the goods and freight charges and total cost comprising all taxes & duties and freight & insurance. Price inclusive of packing and forwarding, applicable GST and other legally permissible duties and levies wherever applicable, handling charges to cover the transport by road from destination railway station to site/ stores, and insurance (transit and storage at site for 45 days).

Since freight is paid extra, goods are required to be delivered at stores/sites in good condition.

13.2	Even though composite price is given, the break-up for all the duties, taxes, freight, insurance, packing and forwarding etc., shall be furnished.

13.3	It is the responsibility of the Bidder to inform himself of the correct rates of duties and taxes leviable on the materials at the time of bidding.

13.4	The proforma credit available to the bidder on the purchases of inputs (raw materials) consequent to the introduction of “MODVAT” Scheme may be taken into account while quoting the prices.

13.5	The Bidder shall indicate on the appropriate Price Schedule (online commercial stage submission) the unit prices (where applicable) and total bid price of the Materials / equipment it proposes to supply under the contract.

Prices indicated on the Price Schedule (On-Line commercial stage) shall be entered separately in the following manner.

The price of the Materials / equipment quoted EXWORKS and all other duties and sales and other taxes payable on the finished Materials / equipment with individual breakup for Taxes and Duties, packing and forwarding, freight and insurance, etc.

14.     Taxes

14.1    	A bidder will be entirely responsible for quoting the correct taxes or levies if any, license fees, etc., he has to incur until completion of the contract. For the purpose of evaluation the bidder should clearly indicate the GST applicable and any other levies payable. Failure to furnish the details leads to loading as indicated in the evaluation criteria.

14.2	If the rates of statutory levies assumed by the Bidder are less than the actual rates prevailing at the time of bidding, the Purchaser will not be responsible for such errors.  If the rates of statutory levies assumed by the Bidder are later proved to be higher than the actual / correct rates prevailing at the time of bidding, the difference will be passed on to the credit of the Purchaser.

14.3.	Deemed Export Benefits: This is not applicable for local purchases with TGSPDCL funds.

15.     	Statutory Variations

Any variation up or down in statutory levy or new levies introduced after signing of the contract under this specification will be to the account of TGSPDCL provided that during delivery schedule. In cases where delivery schedule is not adhered to by the supplier and there are upward variation / revision after the agreed delivered date the supplier will bear the impact of such levies and if there is downward variation / revision, the TGSPDCL will be given credit to that extent.

In case of subvendor items Taxes (GST) are inclusive in tender price. No Statutory variation is applicable. Further price variations in respect of Sub-Vendor items will be considered on tender prices.

This is allowed only once during delivery period i.e., at the time of delivery of goods at factory.

16. 	Bid Currencies:

Prices shall be quoted in Indian Rupees; and will be paid in Indian Rupees Only.

17.	Quantity to quote:

Bidder shall quote a minimum quantity of at least 20% of the total quantity indicated in the bid Specification. Offers less than the minimum prescribed are liable for rejection.

18.	Documents Establishing Bidder’s Eligibility and Qualifications

The Bidder shall furnish, as part of its bid, documents establishing the Bidder's eligibility to bid and its qualifications to perform the contract if its bid is accepted.

The documentary evidence of the Bidder's qualifications to perform the contract if its bid is accepted will establish to the Purchaser's satisfaction:

(a)	that the Bidder has the financial, technical, and production capability necessary to perform the contract;

(b)	that the Bidder meets the qualification criteria listed in Section IV. In addition the Bidder may furnish full particulars regarding supply of the material in question made so far to TGSPDCL during the last 5 years and other reputed utilities.

18.1 	Documents Establishing Materials / equipment Conformity to Bidding Documents.

The Bidder shall furnish as part of its bid, documents establishing conformity to the bidding documents of all Materials / equipment and services, which the Bidder proposes to supply under the Contract.

The documentary evidence of conformity of the Materials / equipment and the services to bidding documents may be in the form of literature, drawings, and data, and will consist of :

(a)  a detailed description of the essential technical and performance characteristics of the Materials /equipment;

(b)	the bidder should specifically mention about furnishing the test certificates and a specimen form of test certificate should be furnished along with the bid.

(c)	a list giving full particulars, including available sources and current prices of spare parts,  special tools etc., necessary for the proper and continuing functioning  of the Materials / equipment following commencement of the use of the Materials / equipment by the Purchaser; and

(d)	an item-by-item commentary on the Purchaser's Technical Specifications demonstrating substantial responsiveness of the Materials / equipment and services to those specifications, or a statement of deviations and exceptions to the provisions of the Technical Specifications.

For purposes of the commentary to be furnished pursuant to above, the Bidder will note that standards for workmanship, material, and equipment, as well as references to brand names or catalogue numbers designated by the Purchaser in its Technical Specifications, are intended to be descriptive only and not restrictive. The Bidder may substitute alternative standards, brand names, and/or catalogue numbers in its bid, provided that it demonstrates to the Purchaser's satisfaction that the substitutions ensure substantial equivalence to those designated in the Technical Specifications.

19.	Bid Security

19.1	The bidder shall furnish, as part of its bid, a Bid security in the amount of 2.36% of the Total Ex-works value of the materials offered against the bid or the amount specified by the Purchaser or part quantity may furnish proportionate bid security

.

19.2	The fact of having enclosed bid security by DD/BG/Online along with the bid should be clearly super scribed on the bid envelope. In case of BG, the bid security is to be furnished for an amount of 2.36% of Total ex-works value.

Bids, which do not have the above superscription, will be rejected and returned to the respective bidders unopened.

19.3	Submission of BID SECURITY by way of cheque, cash, money order, call deposit will not be accepted and will be considered as disqualification.

19.4	Payment of BID SECURITY will be waived at the discretion of the TGSPDCL in the case of fully owned Government undertaking of the Central or State Government.  Such undertakings should immediately apply and obtain exemption before submitting their Bids. They need only refer to the details of such exemption in their Bids. Exemption accorded by any organization other than TGSPDCL will not be considered.

Existing Bid Security exemption deemed to be withdrawn.

19.5	Requests for exemption from payment of BID SECURITY will not be entertained in any other cases.

19.6	Any bid not secured as above will be rejected by the Purchaser.

19.7	Unsuccessful Bidders' Bid Security will be discharged or returned as promptly as possible, but not later than thirty (30) days after the expiration of the period of bid validity prescribed by the Purchaser.

19.8	The successful Bidder's Bid Security will be discharged upon the Bidder signing the contract.

19.9		The Bid Security may be forfeited:

(a)	if a Bidder:

    - Withdraws its bid or alters its prices during the period of bid validity specified by the Bidder on the Bid Form, or

    - Does not accept the correction of errors pursuant to Clause No.30.2; or

    - Offers post Bid rebates, revisions or deviations in quoted prices and / or conditions or any such offers which will give a benefit to the Bidder over others will not only be rejected outright but the original Bid itself will get disqualified on this account and the Bidder’s BID SECURITY will be forfeited.

(b)	In the case of a successful Bidder, if the Bidder fails:

    - To sign the contract in accordance with Clause No.37.

    - To furnish performance security in accordance with Clause No.38.

19.10	In cases where the Bid Cover Contains superscription of having furnished Bid Security by way of DD/BG but if the same is not found within, such Bids will be rejected and bidder will run the risk of being banned.

Note : The bidder shall furnish required Bid Security amount and validity as per specification.  If the bidder fails to furnish bid security amount and bid validity as stipulated in the specification, such tender bid will not be considered for further evaluation.

20.		Period of Validity of Bids.

20.1	Bids shall remain valid for the period of ninety (90) days from the date of bid opening prescribed by the Purchaser. A bid valid for a shorter period will be rejected.

The bidders should clearly super scribe on the sealed envelopes of the bids about the validity. Bids not containing superscription of validity will be rejected and returned unopened.

20.2	In exceptional circumstances, the Purchaser may solicit the Bidder's consent to an extension of the period of validity. The request and the responses there to will be made in writing (or by cable).  The Bid Security provided under Clause No.19 will also be suitably extended. A Bidder may refuse the request without forfeiting its Bid Security.

21. 	GSTR 3B returns:

21.1	Copies of Income Tax, GSTR 3B return and Turnover Tax certificates for the latest period from the appropriate authority will invariably be enclosed to the bid.  In the case of proprietary or partnership firm it will be necessary to produce the certificate / certificates for the proprietor or proprietors and for each of the partners as the case may be.  If the Bidder has already produced the certificate during the calendar year in which the bid is made, it will be sufficient, if particulars are given.

22.	Service Conditions

22.1	The equipment / materials offered will be entirely satisfactory for operation under the climatic conditions indicated below:

(a)	Maximum ambient air temperature (in shade)		450   C

(b)	Maximum ambient air temperature (under sun)		500   C

(c)	Maximum daily average ambient air temperature		350   C

(d)	Maximum yearly average ambient air temperature 	300   C

(e)	Maximum humidity 					100%

(f)	Altitude above M.S.L.					Up to 1000M

(g)	Average No. of thunder storm days per annum		50

(h)	Average No. of dust storm days per annum		Occasional

(i)	Average No. of rainy days / annum			90

(j)	Average Annual Rain fall 				925mm

(k)	Normal tropical monsoon period				4 months

(l)	Maximum wind pressure					150 kg/Sq.M.

22.2	Due consideration will be given to any special devices or attachments put forward by the Bidder which are calculated to enhance the general utility and the safe and efficient operation of the equipment / materials.

23.       Format and Signing of Bid.

23.1	The Bidder shall prepare an original bid, clearly marking "ORIGINAL BID".

23.2	The original bid shall be signed by the Bidder or a person or persons duly authorized to bind the Bidder to the contract.  The person or persons signing the bid will initial all pages of the bid, except for printed literature.

23.3   	Any interlineations, erasures, or overwriting will be valid only if they are initialed by the person or persons signing the bid.

###### D. Submission of Bids

24.	Submission, Sealing and Marking of Bids.

24.1	The tenderers are required to submit their bids in two parts as under:

(i)	Part-I (a) :	Bid Security,  Technical & Qualification Requirements.

(b) :	Technical Bid shall contain full technical particulars and

commercial terms and conditions but without prices.  This

should not contain any cost information whatsoever.

Part-II 	:	Price Bid – containing Price (shall be on-line only)

Bids received with any details pertaining to prices in the offline mode will be liable for rejected

(ii)	The Part-I of the tender should be furnished in a sealed cover superscribing tender enquiry number, name of material, name of the bidder and date of tender opening.

(iii)	Part-I of the bid will be opened on the due date of tender opening. In case the bidders have been granted Bid Security exemption (Clause-19.4), documentary evidence for the same must be furnished.  The firms whose Bid Security is not received as specified in the tender document, the price bids will not be opened and their bids will be rejected summarily.

(iv)	The price bids of only those bidders whose technical bids, on examination, are determined to be technically and commercially acceptable and meeting the specified Qualification Criteria will be opened at a later date.

Sealing and Marking of Bids.

24.2  	The Bidder shall seal the original bid in envelope.

24.3    The inner and outer envelopes will be addressed to the Purchaser.

24.4	The sealed cover as well as the outer envelope should be super scribed as follows:

- Bid Enquiry No.

- Due date and time for online submission.

- Payment of Bid Security

(i)     If paid, give details: D.D. No.      Date:

(ii)    If not paid or exempted, give details.

- Whether 90 days validity offered……….YES / NO

- Whether the quotation is made accepting Payment terms clause …. YES/NO

- Whether the delivery is as per delivery schedule indicated…. YES/NO

- Whether the sample (if specified) has been enclosed/ sent…YES/NO

- Whether the bid is quoted in two parts (clause 24.1)…. (YES/NO)

24.5	Bids not super scribed as above are liable to be rejected.

24.6 	The Bidder shall invariably complete the Bid in full. Details to be furnished by the bidder and Schedule of Prices (to be submitted online only) attached to the specification and enclose the same to the bid without fail.

24.7	The bids shall be in bound volumes (With the documents in the volume not detachable). All pages of the bid except in-amended printed literature shall be initiated by the person/persons signing the bid. The page number shall be referred in Index. All pages including literature, type test reports of the bid shall be numbered and the page numbers shall be continuous. Soft copy of the technical and commercial bids and designs with drawings shall be given in Floppy disc/ CD also. Summary sheet in the given format on the top of the bid duly signed and sealed by the bidder.

24.8	The time of actual receipt in the office only will count for the acceptance of the bid and either the date of bid, date stamp of post office or date stamp of any other office will not count. The TGSPDCL will not be responsible for any postal or any other transit delays.

24.9	Telegraphic quotations will not be entertained under any circumstances. Clarification, amplifications, and / or any other correspondence from the Bidder subsequent to the opening of bid will not be entertained.  The Bidders are advised to ensure that their bids are sent in complete shape at the first instance itself.

24.10	The inner envelopes shall also indicate the name and address of the Bidder to enable the bid to be returned unopened in case it is declared "late".

24.11	If the outer envelope is not sealed and marked as required above, the Purchaser will assume no responsibility for the bid's misplacement or premature opening.

25. 	Deadline for Submission of Bids.

25.1	Bids together with modifications if any, or other withdrawals must be received by the Purchaser not later than the deadline for submission of bids specified in the Salient features of the Bid.

25.2	The Purchaser may, at its discretion, extend this deadline for the submission of bids by amending the bidding documents in which case all rights and obligations of the Purchaser and Bidders previously subject to the deadline will thereafter be subject to the deadline as extended.

26.       Late Bids

26.1	Any bid received by the Purchaser after the deadline for submission of bids prescribed by the Purchaser will be rejected and returned unopened to the Bidder.

26.2     Modification and Withdrawal of Bids.

The Bidder may modify or withdraw its bid after the bid's submission, provided that written notice of the modification, including substitution or withdrawal of the bids, is received by the Purchaser prior to the deadline prescribed for submission of bids.

The Bidder's modification or withdrawal notice will be prepared, sealed, marked, and dispatched. A withdrawal notice may also be sent by cable, but followed by a signed confirmation copy, postmarked not later than the deadline for submission of bids. No bid may be modified after the deadline for submission of bids.

No bid may be withdrawn in the interval between the deadline for submission of bids and the expiration of the period of bid validity specified. Withdrawal of a bid during this interval may result in the forfeiture of its Bid Security.

###### E. 	Opening and Evaluation of Bids

27.       Opening of Bids by the Purchaser

27.1	The Purchaser will open all bids meeting above criteria, at the time, on the date, and at the place specified.

27.2   	The Bidders' names, bid modifications or withdrawals, discounts, and the presence or absence of requisite Bid Security and such other details as the Purchaser, at its discretion, may consider appropriate, will be announced at the opening.

27.3   	Bids that are not opened and read out at bid opening will not be considered further for evaluation, irrespective of the circumstances.

28.	     Clarification of Bids

28.1	During evaluation of the bids, the Purchaser may, at its discretion, ask the Bidder for a clarification of its, bid.  The request for clarification and the response shall be in writing, and no change in the prices or substance of the bid shall be sought, offered, or permitted.

29.	    Preliminary Examination

29.1	The Purchaser will examine the bids to determine whether they are complete, whether any computational errors have been made, whether required sureties have been furnished, whether the documents have been properly signed, and whether the bids are generally in order.

29.2 	Arithmetical errors will be rectified on the following basis.  If there is a discrepancy between the unit price and the total price that is obtained by multiplying the unit price and quantity, the unit price will prevail, and the total price will be corrected.  If the Supplier does not accept the correction of the errors, its bid will be rejected, and its Bid Security may be forfeited.  If there is a discrepancy between words and figures, the amount in words will prevail.  If the supplier does not accept the correction of the errors, its bid will be rejected and its Bid Security may be forfeited.

29.3  	The Purchaser may waive any minor informality, nonconformity, or irregularity in bid which does not constitute a material deviation, provided such waiver doesn't prejudice or affect the relative ranking of any Bidder.

29.4  	Prior to the detailed evaluation, the Purchaser will determine the substantial responsiveness of each bid to the bidding documents.  For purposes of these Clauses, a substantially responsive bid is one, which conforms to all the terms and conditions of the bidding documents without material deviations.  Deviations from, or objections or reservations to critical provisions, such as those concerning Bid Security, and applicable GST will be deemed to be a material deviation.  The Purchaser's determination of a bid's responsiveness is to be based on the contents of the bid itself without recourse to extrinsic evidence.

29.5   	If a bid is not substantially responsive, it will be rejected by the Purchaser and may not subsequently be made responsive by the Bidder by correction of the nonconformity.

Note : Payment terms, Delivery period, Performance Bank Guarantee, applicable GST” should be in line with the terms and conditions of the specification. If any bidder does not meet any one of the conditions, such tender will not be considered. Please note that the conditional offers are also not considered. Hence the bidder shall submit the tender in line with the terms and conditions of the specification.

30.	Evaluation and Comparison of Bids.

30.1	The Purchaser will evaluate and compare the bids, which have been determined to be Substantially responsive.

30.2	The Purchaser's evaluation of a bid will take into consideration one or more of the following factors

All the bids, which are opened and considered for evaluation will be checked for qualification requirements in respect of technical and commercial aspects. Such of the bids, which do not meet the qualification requirements, will not be evaluated further. The bid is to be checked for its conformity to the technical specification. If it does not meet the technical specification, the Bid will not be evaluated further. However, if in the opinion of the purchaser the bidder has offered equipment / material better than the technical specification the same may be considered. The bid may be rejected for the following reasons:

      - Not in the prescribed form

      - Insufficient bid security or bid not accompanied by the required bid security or proof of  bid security  exemption

      - Bids not properly signed

      - The bidder is a vendor who is banned from further business transactions and the period of ban is still in force.

      - Bid received after the due date and time

      - The bid is through telegram or fax

- Further, the purchaser may enquire from the bidder in writing for any clarification of the bid. The response of the bidder will also be in writing. However no change in the prices or substance of the bid will be sought, offered or permitted.

- Bids will be examined for completeness and for any computational errors.

- Arithmetical errors will be rectified on the following basis.

  - Where there is a discrepancy between the unit price and total price, the unit price will prevail and the total price will be corrected accordingly.

  - Where there is a discrepancy between words and figures, the amount in words will prevail.

  - Failure on the part of the bidder to agree to the above corrections will result in rejection of his offer and forfeiture of his bid security.

- It will be ensured that the required sureties have been furnished and that the documents have been properly signed.

- The purchaser's evaluation of a bid will take into consideration one or more of the following factors

(a)	Delivery schedule offered in the bid;

(b)	Deviations in payment schedule from that specified in the general terms and conditions of the contract and technical deviations.

(c)	The cost of components, mandatory spare parts, and service;

(d)	The availability of spare parts and after-sales services for the equipment offered in the Bid;

(e)	The projected operating and maintenance costs during the life of the equipment;

(f)	 The performance and productivity of the equipment offered;

(g)          Other specific criteria indicated in the Bidding documents.

In addition the Purchaser’s evaluation of a bid will take into account the net landed cost of the material at the final destination. For the purpose of evaluation net landed cost is arrived at by adding all elements of the basic price, allowable discount & any other levies, packing & forwarding, freight charges, insurance (transit & storage) as quoted by the bidder, interest on advance if any, erection, servicing and other charges and applicable GST as called for.

In addition any variation up or down in GST/ new levies introduced subsequent to bid opening and before award will be considered for comparison purposes.

The following criteria may be adopted for GST for evaluation

  - It is the responsibility of the bidder to quote all taxes (GST) correctly without leaving any column unfilled.  Where GST is not applicable, the bidder should enter “NA”.  If no GST is leviable the same may be entered as “NIL”. If any column is left blank or filled vaguely like “as applicable”, the same will be loaded with the maximum of the other eligible Bids.

  - Where there is an exemption of GST, the documentary evidence to that effect will be enclosed by the supplier.

  - The bidders for supply and works shall invariably possess the TIN No. & PAN No. for the bids above Rs.5.00 Lakhs and this must be verified before entering into contract.

- Prior to detailed evaluation, the responsiveness of each bid will be determined. A substantially responsive bid is one that conforms to all the terms and conditions of the bidding documents without material deviations. For this purpose superscription, qualification requirement, bid security, validity, delivery, payment terms, price schedule, GST will be deemed to be the critical provisions and deviations in any one of these items will be deemed to be a material deviation.

The purchaser may waive any minor informality, non-conformity or irregularity in the bid which does not constitute a material deviation, provided such waiver does not affect the relative ranking of any bidder.  The purchaser will clearly indicate in the bid specification the methodology for evaluation of bids.

(a)	Bid price, which will include all, costs of manufacture and services at manufacturing place as well as, Transportation to destination stores, packing and forwarding, insurance and all Taxes & other legally permissible duties & levies payable.

(b)	Delivery schedule offered in the bid.

(c)	Deviations in payment schedule from that specified in the general terms and conditions of the contract.

(d)	The cost of components, mandatory spare parts, and service

(e)	The availability of spare parts and after-sales services for the equipment offered in the Bid;

(f)	The projected operating and maintenance costs during the life of the equipment;

(g)	The performance and productivity of the equipment offered; and/or

- Other specific criteria indicated in the Bid Specification.

30.3(a) The Purchaser’s evaluation of a bid will take into account the Net Landed Cost of the Material at destination stores applicable GST quoted by the Bidder.  It is the responsibility of the bidder to quote all GST correctly without leaving any column unfilled.  Where not applicable the column may be filled as “NA”.  If no GST is le-viable the same may be filled as “NIL”. If any column is left blank the same is loaded with maximum of other eligible Bids.

30.3(b) Any statutory variations of GST and new levies imposed after opening of the bid and before award of the contract will be taken into consideration for the purpose of evaluation.

30.4	A substantially responsive bid is one, which conforms to all the terms and conditions of the bidding documents without material deviations. For this purpose superscription, qualification requirement, bid security, validity, delivery, payment terms, price schedule, GST will be deemed to the critical provisions and deviations in any one of these things will be deemed to be a material deviation.

31.	Contacting the Purchaser.

31.1	From the time of the bid opening to the time of contract award, if any Bidder wishes to contact the Purchaser on any matter related to the bid, it should do so in writing.

31.2	Any effort by a Bidder to influence the Purchaser in its decisions on bid evaluation, bid comparison, or contract award will result in the rejection of the Bidder's bid.

F. 	Award of Contract.

32.       Post Qualification

32.1	In the absence of pre-qualification, the Purchaser will determine to its satisfaction whether the Bidder that is selected as having submitted the lowest evaluated responsive bid is qualified to perform the contract satisfactorily.

32.2  	The determination will take into account the Bidder's financial, and production capabilities. It will be based upon an examination of the documentary evidence of the Bidder's qualification submitted by the Bidder, as well as such other information as the Purchaser deems necessary and appropriate.

33.	Award Criteria:

33.1	The Purchaser will award the contract to the successful Bidder / Bidders whose bid has / have been determined to be substantially responsive.

34.	Purchaser’s Right to Vary Quantities at Time of Award

34.1	The Purchaser reserves the right at the time of contract award to increase or decrease upto 50%, the quantity of Materials / equipment and services originally specified in the Schedule of Requirements without any change in unit price or other terms and conditions.

34.2	The purchaser reserves the right to vary the ordered quantity by +/- 50% during the execution of the contract.

35.	Purchaser's Right to Accept Any Bid and to Reject Any or All Bids

35.1   	The Purchaser reserves the right to accept or reject any bid, and to annul the bidding process and reject all bids at any time prior to contract award, without thereby incurring any liability to the affected Bidder or Bidders or any obligation to inform the affected Bidder or Bidders.

36.	Notification of Award

36.1	Prior to the expiration of the period of bid validity, the Purchaser will notify the Successful Bidder in writing by registered letter or by cable, to be confirmed in writing by registered letter, that its bid has been accepted.

36.2	The notification of award will constitute the formation of the Contract.

36.3  	Upon the successful Bidder's furnishing of the performance security, the Purchaser enters into contract with successful Bidder / Bidders. The Purchaser will notify each unsuccessful Bidder and will discharge its Bid Security.

37.	Signing of Contract:

The Purchaser notifies the successful Bidder that its bid has been accepted. Within 30 (thirty days) of receipt of notification of award of Contract, the successful Bidder will sign and date the contract. Failure to comply with this stipulation will entail cancellation of the contract besides forfeiture of the bid security.

38.	Performance Security:

38.1   	Within Fifteen (15) days of receipt of the notification of Contract award. The successful Bidder will furnish to the Purchaser the performance security for an amount 10% of the contract value for proper fulfillment of the contract, which will include the warranty period, and completion of performance obligations including Warranty obligations. The Performance Security will cover   60 days beyond the date of completion of performance obligations including Warranty obligations.

In the event of any correction of defects or replacement of defective material during the warranty period, the warranty for the corrected / replaced material will be extended to a further period of 12 months and the Performance Bank Guarantee for proportionate value will be extended          60 days over and above the extended warranty period.

38.2 	The proceeds of the performance security will be payable to the Purchaser as compensation for any loss resulting from the Supplier's failure to complete its obligations under the Contract.

38.3 	The performance security will be…

- A bank guarantee issued by a nationalized/Scheduled bank acceptable to the Purchaser, in the form provided in the bidding documents.

- A banker's cheque or crossed DD or Pay Order payable at the Head quarter of    the Purchaser in favour of the Purchaser drawn on any Nationalized/ scheduled bank.

38.4   	The performance security will be discharged by the Purchaser and returned to the Supplier not later than sixty (60) days after the expiry date.

38.5   	Failure of the successful Bidder to comply with the above requirement will entail cancellation of the award and forfeiture of the Bid Security and the balance to make up the performance security deposit will be deducted from pending payments if any due to the tenderer from TGSPDCL on other orders in addition the company will also become liable for being blacklisted by TGSPDCL.

39.	Corrupt or Fraudulent Practices

It is essential that the Purchaser as well as Bidder / supplier / contractor for the purposes of this provision, the terms set forth below as follows:

(i) “Corrupt practice” means the offering, giving, receiving or soliciting of any thing of value to influence the action of a public official in the procurement process or in contract execution, and

(ii) “Fraudulent practice” means a misrepresentation of facts in order to influence a procurement process or the execution of a contract to the determinant of the purchaser, and includes collusive practice among Bidders (prior to or after bid submission) designed to establish bid prices at artificial non-competitive levels and to deprive the purchaser of the benefits of free and open competition;

(iii) Will reject a proposal for award if it determines that the Bidder recommended for award has engaged in corrupt or fraudulent practices in competing for the contract in question;

(iv) Will declare a firm ineligible, either indefinitely or for a stated period of time, to be awarded a contract if it at anytime determines that the firm has engaged in corrupt or fraudulent practices in competing for, or in executing, a contract.

40.		Use of Contract Documents and Information:

40.1	The Supplier will not, without the Purchaser's prior written consent, disclose the Contract, or any provision thereof, of any specification, plan, drawing, pattern, sample, or information furnished by or on behalf of the Purchaser in connection therewith, to any person other than a person employed by the Supplier in the performance of the Contract.  Disclosure to any such employed person will be made in confidence and will extend only so far as may be necessary for purposes of such performance.

40.2	The Supplier will not, without the Purchaser's prior written consent, make use of any document or information except for purposes of performing the Contract.

40.3	Any document, other than the Contract itself, will remain the property of the Purchaser and will be returned ( in all copies) to the Purchaser on completion of the supplier's performance under the Contract if so required by the Purchaser.

40.4    The Supplier will permit the Purchaser or his authorized representative to inspect the Supplier’s accounts and records relating to the performance of the Supplier and to have them audited by auditors appointed by the Supplier.

41.	Patent Rights

41.1	The Supplier will indemnify the Purchaser against all third-party claims of infringement of patent, trademark, or industrial design rights arising from use of the Materials / equipment or any part thereof.

42.	Places / Locations:

42.1	Particulars of site location and nearest rail heads to which the equipments / material have to be supplied will be given to successful Bidders.

43.	Delivery:

43.1	Delivery period will be reckoned from the date of signing of the contract. The delivery quoted will be firm, definite, unconditional and on the basis of receipt of materials at destination in good condition without any bearing on the procurement of raw materials or any similar prerequisites.  The commencement date and date of delivery will be indicated. The preferred delivery time, which is the essence of this specification, is indicated in the schedule. Final deliveries are however, subject to confirmation at the time of Contract.  Delay in delivery of materials FADS – (Free At Destination Store) due to non-availability of railway booking, non-allotment of wagons and any such reasons will not be considered.  It is the responsibility of the supplier to make alternative arrangements for transporting the materials by road or rail so as to see that the material reaches the destination within the stipulated period.  The Purchaser reserves its right to defer the delivery date at any time after orders are placed without any change in the conclusion of contract other conditions supply.  The delivery period, which will be reckoned from the date of the Contract, will be guaranteed under penalty as in Clause 59.

44.     Inspections and Tests

(i) The supplier will keep the Purchaser informed in advance of the time of the   starting and the 	progress of manufacture of equipment in its various stages so that arrangement could be made for 	inspection. The accredited representative of the TGSPDCL will have access to the supplier’s or 	his subcontractor’s work at any time during working hours for the purpose of inspecting the 	materials during manufacturing of the materials/equipment and testing and may select test 	samples from the materials going into plant and equipment. The supplier will provide the 	facilities for testing such samples at any time including access to drawings and production data at 	no charge to Purchaser.  As soon as the materials are ready the supplier will duly send intimation 	to TGSPDCL by Registered Post and carry out the tests in the presence of representative of the 	TGSPDCL.

(ii)	The TGSPDCL may at its option get the materials inspected by the third party if it feels necessary and all inspection charges in this connection will be borne by the TGSPDCL. In case of material, not of acceptable quality or not conforming to the specification, the materials will be rejected.  You have to re-offer the material for inspection.  In such a case the 2nd inspection charges are to the suppliers account. In case the materials are rejected in the 2nd inspection also, the TGSPDCL reserves the right to cancel the order.

(iii)	The dispatches will be affected only if the test results comply with the specification. The dispatches will be made only after the inspection by the TGSPDCL representative Officer is completed to the TGSPDCL satisfaction or such inspection is waived by the competent authority.

(iv)	 The acceptance of any quantity of materials will in no way relieve the supplier of its    responsibility for meeting all the requirements of this specification and will not prevent subsequent rejection if such materials are later found to be defective.

(v)  The supplier will give 15 days advance intimation to enable the Purchaser to depute his representative for witnessing the acceptance and routine tests.

(vi)	 Should any inspected or tested materials / equipment fail to conform to the specification, the Purchaser may reject the materials and supplier will either replace the rejected materials or make alterations necessary to meet specifications requirements free of costs to the Purchaser.

(vii) In the case of transformers, instrument transformers and meters, inspection will be conducted every year, for the first 5 years on a 2% sample of the quantities supplied. Samples will be collected at random to establish that the guaranteed technical parameters are as per the submitted bid by the supplier. In the case of non-adherence, the purchaser may take suitable action on the supplier including cancellation of vendor registration and banning further dealings, depending on the gravity of the deviation. These random inspections may be entrusted to a third party.

(viii)Inspection not carried OUT due to non-readiness of the material even after 	contacting/confirmed over phone from 	the supplier about availability of material and 	physical verification at the supplier premises, the charges @ 0.25% of Ex-works price of 	material offered for inspection (inclusive of GST, traveling expenses, boarding 	and lodging       charges at the place of inspection and all  incidental charges) shall  be paid by supplier subject to a maximum of Rs.10,000.00 .

45.	Name Plate:

Equipment should be provided with name plate giving full details of manufacture, capacities and other details as specified in the relevant IS or other specification stipulated.  The contract No. and date and year of supply and the words “TGSPDCL” must be etched on the name plate.

46.	Packing

46.1	The Supplier will provide such packing of the Materials / equipment as is required to prevent their damage or deterioration during transit to their final destination, as indicated in the Contract. The packing will be sufficient to withstand, without limitation, rough handling during transit and exposure to extreme temperatures, salt and precipitation during transit, and open storage.  Packing case size and weights will take into consideration, where appropriate, the remoteness of the Materials / equipment' final destination and the absence of heavy handling facilities at all points in transit.

46.2 	The packing, marking, and documentation and outside the packages will comply strictly with such special requirements as will be expressly provided for in the Contract and in any subsequent instructions ordered by the Purchaser. The supplier will be required to make separate packages for each consignee; each package will be marked on three sides with proper paint / indelible ink with the following;

- Contract Number

  - Supplier’s name

  - Packing list reference number

46.3   The supplier, whenever dispatches material to a destination should prepare the following information in the form of packing slip in quadruplicate and send the same to the consignee and obtain his acknowledgement. The consignee will return to the supplier one copy of the packing slip with his remarks.  The proforma of packing slip will be as follows:

# PACKING SLIP

- Contract No. & Date.

- Quantity allotted to the stores and rate applicable.

- Quantity so far supplied to the stores and the rate applied.

- Quantity now supplied and the rate applied.

- Total quantity supplied under the Contract with rates applied.

- Programme for supplying the balance quantity to the Stores.

47.        Delivery Documents

47.1	Delivery of the Materials/equipment will be made by the Supplier in accordance with the terms specified in the contract.

The latest test certificates containing the result of the tests as per the relevant IS or other specification stipulated must be submitted to the Chief General Manager (P&MM) and got approved by him.

47.2	Documents to be submitted by the Supplier are specified as under…

(i)  	Insurance certificate;

(ii)	Supplier’s certificate certifying that the defects if any pointed out during inspection have been rectified (3 copies).

(iii)	Manuals in Six sets and one set of reproducible drawings.

The Purchaser will receive the above documents soon after the dispatch of materials and if not received, the supplier will be responsible for any consequent expenses.

48.     	Insurance

48.1 	The Materials / equipment supplied under the Contract will be fully insured against loss or damage incidental to manufacture or acquisition, transportation and delivery and also storage for 45 days at destination stores before taking into stock.

48.2 	The bidder shall a) Initiate and pursue insurance claim till settlement, and b) Promptly arrange for repair and/or replacement of any damaged items in full irrespective of settlement of insurance claim by the under Writers. c) All costs because of insurance liabilities covered under the contract will be to supplier’s account. The supplier shall provide the Purchaser with a copy of all insurance policies and documents taken out by him in pursuance of the ‘Contract’. Such copies of documents shall be submitted to the purchaser immediately after such insurance coverage. The supplier shall also inform the Purchaser in writing at least sixty (60) days in advance, regarding the expiry, cancellation and/or change in any of such documents and ensure revalidation/renewal etc., as may be necessary well in time.

The risks that are to be covered under the insurance shall be comprehensive and shall include but not limited to, the loss or damage in transit, storage, due to theft, pilferage, riot, civil commotion, weather conditions, accident of all kinds, fire, flood, war risk (during ocean transportation) bad or rough handling etc. The scope of such insurance shall cover the entire contract value.

The insurance will be in an amount equal to 100% FADS value of Materials / equipment on all risks basis. The policy will have a provision for extension to cover further storage if necessary at destination stores / site at TGSPDCL cost. The insurance beneficiary shall be of TGSPDCL.

49.	Transportation

49.1  	The Supplier is required under the Contract to transport the Materials / equipment to a specified place of destination defined as normally the district stores, transport to such place of destination, including insurance and storage, will be arranged by the Supplier, and the related costs will be included in the Contract Price only.

50.       Incidental Services

50.1	The Supplier may be required to provide any or all of the following services, including additional services, if any.

(a)	Performance or supervision of on-site assembly and/or start-up of the supplied Materials / equipment;

(b)	Furnishing of tools required for assembly and/or maintenance of the supplied Materials / equipment;

(c)	Furnishing of a detailed operations and maintenance manual for each appropriate unit of the supplied Materials / equipment;

(d)	Performance or supervision or maintenance and/or repair of the supplied Materials / equipment, during warranty period, provided that this service will not relieve the Supplier of any warranty obligations under this contract; and

(e)	Training of the Purchaser's personnel, at the Suppliers' plant and/or on-site, in assembly, start-up, operation, maintenance, and/or repair of the supplied Materials / equipment.

51.  	Spare Parts

51.1 	The Supplier may be required to provide any or all of the following materials, notifications, and information pertaining to spare parts manufactured or distributed by the Supplier.

        - Such spare parts as the Purchaser may choose to purchase from the Supplier, provided that this election will not relieve the supplier of any warranty obligations under the contract; and

        - In the event of termination of production of the spare parts:

        - Advance notification to the Purchaser of the impending termination.

        - Time to permit the Purchaser to procure needed requirement; and following such termination, furnishing at no cost to the Purchaser, the blueprints, drawings, and specifications of the spare parts, if requested.

52.	Warranty

52.1	The supplier will warrant for the satisfactory functioning of the material/equipment as per specification for a minimum period of 18 months from the date of receipt of the material/equipment in good condition.

52.2	The Supplier warrants that the Materials / equipment supplied under the Contract are new, unused, of the most recent or current models, and that they incorporate all recent improvements in design and materials unless provided otherwise the special guarantee sought in technical specification. The supplier further warrants that all Materials / equipment supplied under this Contract will have no defect, arising from a design and / or materials as required by the Purchaser's specifications or from any act of omission of the Supplier, that may develop under normal use of the supplied Materials / equipment.

52.3	All the materials will be of the best class and will be capable of satisfactory operation in the tropics under service conditions indicated in clause 22.1 without distortion or deterioration.  No welding filling or plugging of defective parts will be permitted, unless otherwise specified, they will conform to the requirements of the appropriate Indian, British or American Standards. (Where a standard specification covering the material in question has not been published, the standards of the American Society for testing of Materials should be followed).

52.4	The entire designs and construction will be capable of withstanding the severest stresses likely to occur in actual service and of resisting rough handling during transport.

52.5	Unless otherwise specified the warranty period will be 18 months from the date of acceptance of the Materials / equipment. The Supplier will, in addition, comply with the performance guarantees specified under the contract. If, for reasons attributable to the Supplier, these guarantees are not attained in whole or in part, the supplier will at its discretion either, Make such changes, modifications, and/or additions to the Materials / equipment or any part thereof as may be necessary in order to attain the contractual guarantees specified in the contract at its own cost and expense and to carry out further performance tests as per the relevant standards.

52.6	The Purchaser will promptly notify the supplier in writing of any claims arising under this warranty.

52.7  	"Upon receipt of such notice, the Supplier will within 30 days repair or replace the defective Materials / equipment or parts thereof, free of cost at the ultimate destination. The supplier will take over the replaced parts/Materials/equipment at the time of their replacement.  No claim whatsoever will lie on the Purchaser for the replaced parts/Materials /equipment thereafter". In the event of any correction of defects or replacement of defective material during the warranty period, the warranty for the corrected/replaced material will be extended to a further period of           12 months.

52.8   	If the Supplier, having been notified, fails to remedy the defect(s) within the above period, the Purchaser may proceed to take such remedial action as may be necessary, at the Supplier's risk and expense duly deducting the expenditure from subsequent bills / bank guarantee and without prejudice to any other rights which the Purchaser may have against the Supplier under the Contract.

53.	Payment

53.1 	100% payment along with F&I, GST will be made on or after 30 days reckoned from the date of receipt of material/ equipment at destination/ stores (i.e., 103 entry in SAP module), duly transferring the said amount to the bank account of the supplier by the purchaser bank. The supplier will have to predefine the Bank Account details before entering into contract for electronic transfer of Payments.

53.2  	The 100% payment mentioned above is subject to on submission of performance security as per Clause 38 by the supplier.

53.3	The supplier should invariably submit test certificates and other documents, the purchaser specifies as soon as dispatch is made so that they can be checked and approved well in advance.

53.4	The performance guarantee to be executed in accordance with this specification will be furnished on a stamp paper of value Rs.100/-.  The Bank Guarantee will be extended if required suitably. In accordance with the provisions of Clause No.38.

53.5  	 If the supplier has received any over payments by mistake or if any amounts are due to the TGSPDCL due to any other reason, when it is not possible to recover such amounts under the contract resulting out of this specification, the TGSPDCL reserves the right to collect the same from any other amount and / or Bank Guarantees given by the company due to or with the TGSPDCL.

53.6   	When the supplier does not at any time, fulfill his obligations in replacing/rectifying etc. of the damaged/defective materials in part or whole promptly to the satisfaction of the TGSPDCL Officers, the TGSPDCL reserves the right not to accept the bills against subsequent dispatches made by the supplier and only the supplier will be responsible for any demurrages, wharfages or damage occurring to the consignments so dispatched.

54.     	Prices

54.1	Prices charged by the Supplier for Materials / equipment delivered and Services performed under the Contract will not vary from the prices quoted by the supplier in its bid, with the exception of any price adjustment authorized in the contract.

55.	Change Orders

55.1	The Purchaser may at any time, by a written order given to the Supplier make changes within the general scope of the Contract   in any one or more of the following:

- Drawings, designs, or specifications, where Materials / equipment to be furnished under the Contract are to be specifically manufactured for the Purchaser;

- The method of shipment or packing;

- The place of delivery; and/or

- The Services to be provided by the Supplier.

56.	Contract Amendments

56.1	No variation in or modification of the terms of the Contract will be made except by written amendment by the Purchaser and accepted by the supplier.

57.	Assignment

57.1	The Supplier will not assign, in whole or in part, its obligations to perform under this Contract, except with the Purchaser's prior written consent.

58.	Delays in Supplier’s Performance

58.1	Delivery of the Materials / equipment will be made by the Supplier in accordance with the time schedule prescribed by the Purchaser in the Schedule of Requirements.

58.2   	If at any time during performance of the Contract, the Supplier should encounter conditions impeding timely delivery of the Materials / equipment, the Supplier will promptly notify the Purchaser in writing of the fact of the delay, its likely duration and its cause(s). As soon as practicable after receipt of the Supplier's notice, the Purchaser will evaluate the situation and may at its discretion extend the Supplier's time for performance, with or without liquidated damages, in which case the extension will be ratified by the parties by amendment of the Contract.

58.3   	Except as provided under force majeure clause a delay by the Supplier in the performance of its delivery obligations will render the Supplier liable to the imposition of liquidated damages unless an extension of time is agreed upon without the application of liquidated damages.

58.4	“Not withstanding anything to the contrary herein and to the extent permitted by the 	law, the aggregate liability of Bidder to the Employer, whether in contract, tort (including negligence) or otherwise, will be limited to 100% of the total contract 	value.”

59.		Penalty for delay in supplies

The time for and the dates for delivery mentioned in the contract will be deemed to be the essence of the contract.  Subject to force majeure Clause No.64, if the Supplier fails to deliver any or all of the Materials / equipment or to perform the Services within the period(s) specified in the Contract, the Purchaser will, without prejudice to its other remedies under the Contract, deduct from the Contract Price, as liquidated   damages, a sum equivalent to 0.5% per week on the undelivered portion subject to a maximum of 5% of the cost of the undelivered portion within the scheduled time. The number of days would be rounded off to the nearest week and penalty calculated accordingly. Once the maximum is reached the Purchaser may consider termination of the contract.

The check measurement date i.e., the date of receipt of materials at destination stores in good condition will be taken as the date of delivery. For calculation of penalty, the date of receipt of material at the destination stores is the date of delivery subject to the condition that the goods/ material is received in good condition. Materials/Equipment which are not of acceptable quality or are not confirming to the specification would be deemed to be not delivered. For penalty, the number of days would be rounded off to the nearest week and penalty calculated accordingly.

The penalty specified above will be levied and would be adjusted against subsequent pending bills.

In cases where new vendors fail to meet the requirement of the Contract there would be no penalty to such vendors but they will be excluded from the next bid for the particular item of the material.

Any failure on the part of new vendors for a second time would cause them to be removed from the list of registered vendors.

60.     RISK PURCHASE:

Incase of supplier who has not adhered to the delivery schedule, the TGSPDCL reserves the right 	to purchase the balance quantity from the open market/floating another tender and recover the 	extra expenditure thus incurred from the supplier.

61.     Termination for Default

61.1	The Purchaser, without prejudice to any other remedy for breach of Contract, by written notice of default sent to the Supplier, may terminate this Contract in whole or in part:

i.  If the Supplier fails to deliver any or all of the Materials / equipment within the period(s)

specified in   the Contract, or  within any extension thereof granted by the Purchaser.

ii.   If the Supplier fails to perform any other obligation(s) under the Contract.

iii.  If the Supplier, in the judgment of the Purchaser has engaged in corrupt or fraudulent

practices in competing for or in executing the Contract.

61.2  	In the event the Purchaser terminates the Contract in whole or in part, the Purchaser may procure, upon such terms and in such manner, as it deems appropriate, Materials / equipment or services similar to those undelivered, and the Supplier will be liable to the Purchaser for any excess costs for such similar Materials / equipment or Services. However, the Supplier will continue performance of the Contract to the extent not terminated.

62.	Termination for Insolvency

62.1   	The Purchaser may at any time terminate the Contract by giving written notice to the Supplier if the Supplier becomes bankrupt or otherwise insolvent. In this event, termination will be without compensation to the supplier, provided that such termination will not prejudice or not affect any right of action or remedy, which has accrued or will accrue thereafter to the Purchaser.

63.	Termination for Convenience

63.1 	The Purchaser, by written notice sent to the Supplier, may terminate the Contract, in whole or in part, at any time for its convenience. The notice of termination will specify the termination is for the Purchaser's convenience, the extent to which performance of the supplier under the Contract is terminated, and date upon which termination becomes effective.

63.2	However the Materials / equipment that are complete and ready for shipment within thirty (30) 	days after the supplier's receipt of notice of termination will be accepted by the Purchaser at 	the 	Contract terms and prices.

64.	Force Majeure

64.1	The Supplier will not be liable for forfeiture of its performance security, penalty for late delivery, or termination for default if and to the extent that its delay in performance or other failure to perform its obligations under the Contact is the result of an event of Force Majeure.

64.2  	 For purposes of this clause, "Force Majeure" means an event beyond the control of the Supplier and not involving the Supplier's fault or negligence and not foreseeable.  Such events may include, but are not restricted to, wars or revolutions fires, floods, epidemics, quarantine restrictions, and freight embargoes.

64.3   	If a Force Majeure situation arises, the supplier will promptly notify the Purchaser in writing of such condition and the cause thereof.  Unless otherwise directed by the Purchaser in writing, the Supplier will continue to perform its obligations under the Contract as far as is reasonably practice, and will seek all reasonable alternative means for performance not prevented by the Force Majeure event.

No price variance will be allowed during the period of force majeure.

65.	Settlement of Disputes

65.1	If any dispute or difference of any kind whatsoever will arise between the Purchaser and the Supplier in connection with or arising out of the Contract, the parties will make every effort to resolve amicably such dispute or difference by mutual consultation.

65.2	If, after thirty (30) days the parties have failed to resolve their dispute or difference by such mutual consultation, then either the Purchaser or the Supplier may give notice to the other party of its intention to commence arbitration, as hereinafter provided, as to the matter in dispute, and no arbitration in respect of this matter may be commenced unless such notice is given.

65.3	Any dispute of difference in respect of which a notice of intention to commence arbitration has been given in accordance with this Clause will be finally settled by arbitration.  Arbitration may be commenced prior to or after delivery of the Materials / equipment under the Contract.

65.4	Arbitration proceedings will be conducted in accordance with the following rules of procedure. The dispute resolution mechanism will be as follows:

(a) 	In the case of a dispute or difference arising between the Purchaser and a Supplier relating to any matter arising out of or connected with this agreement, such dispute or difference will be settled in accordance with the Arbitration and Conciliation Act. 1996.  The Arbitral Tribunal will consist of three Arbitrators one each to be appointed by the Purchaser and the supplier the Third Arbitrator will be chosen by the two Arbitrators so appointed by the parties and will act as Presiding Arbitrator. In case of failure of the two Arbitrators appointed by the parties to reach upon a consensus within a period of 30 days from the appointment of the Arbitrator appointed subsequently, the Presiding Arbitrator will be appointed by The Institution of Engineers (India).

(b)	If one of the Parties fails to appoint its Arbitrator in pursuance of Sub-Clause (a) within 30 days after receipt of the notice of the appointment of its Arbitrator by The Institution of Engineers (India), will appoint the Arbitrator. A certified copy of the order of the Institution of Engineers (India), making such an appointment will be furnished to each to the parties.

(c) 	Arbitration Proceedings will be held at Purchaser’s Headquarters, and the language of the Arbitration Proceedings and that of all documents and communication between the parties will be English.

(d ) 	The decision of the majority of Arbitrators will be final and binding upon both parties.  The cost and expenses of Arbitration Proceedings will be paid as determined by the Arbitral Tribunal.  However, the expenses incurred by each party in connection with the preparation, presentation etc., of its proceedings as also the fees and expenses paid to the Arbitrator appointed by such party or on its behalf will be borne by each party itself.

- Where the value of the Contract is Rs. One Crore and below, the disputes or differences arising will be referred to the Sole Arbitrator.  The Sole Arbitrator should be appointed by agreement between the parties; failing such agreement, by the appointing authority namely The Institution of Engineers (India).

65.5	Notwithstanding any reference to arbitration herein,

- The parties will continue to perform their respective obligations under the Contract unless they otherwise agree; and

- The Purchaser will pay the Supplier any monies due to the Supplier.

66.		Jurisdiction

66.1	All and any disputes or differences arising out of or touching this contract will be decided by the Courts or Tribunals situated in Purchaser’s Headquarters only. No suit or other legal proceedings will be instituted elsewhere.

67.    	Notices

67.1	Any notice given by one party to the other pursuant to this Contract will be sent to the other party in writing or by cable, telex, or facsimile and confirmed in writing to the other party’s address.

67.2  	A notice will be effective when delivered or on the notice's effective date, whichever is later.

68.	Foreign Exchange

68.1	No Foreign Exchange is available or expected for this purchase. Offers which do not require release of F.E. or procurement of import license by TGSPDCL only will be considered. Where some of the components are to be imported the manufacturer will have to make their own arrangements for import license etc., and should not look for any assistance from TGSPDCL.

SECTION – IV

SPECIFICATION NO. STN-1176/24-25

SCHEDULE OF MATERIALS

| Sl. No. | Description of Material | Qty. (Nos.) | Stores |
| --- | --- | --- | --- |
| 1 | 11kV 200 A Load break outdoor tilting type 3 pole gang operated vertical mounted Air – break switches with 6 Nos. Post type insulators Polymer type through a hollow square pipe coupling of 25x25 sqmm as per drawing D-1, D-2, D-3 & D-4 with all accessories for assembly and operation as per the specification and as per the standards mentioned at Section-V. | 10,000 | FADS at TGSPDCL stores |

Note: -	(1)  The Firm prices shall be quoted

(2)  The quantity of monthly delivery may be quoted.

(3)  Delivery shall commence within 45 days from the date of receipt of purchase order

and complete within three (3) months thereafter. However the delivery schedule may vary based on TGSPDCL requirement. The rate of monthly delivery may be quoted.

(4) The tenderer should quote the rates for free at TGSPDCL destination stores.

(5) The quantities mentioned above are to be supplied to suit TGSPDCL requirements.

-SD/-

CHIEF GENERAL MANAGER/P&MM

SECTION-V

(STN-1176/24-25)

TECHNICAL SPECIFICATION FOR 11KV 200A (TT) GANG OPERATED LOAD BREAK AB SWITCHES WITH POST TYPE POLYMER INSULATORS

1.  SCOPE :-

The specification provides for the manufacture, testing before dispatch, supply and delivery in full shape at destination stores of 3 Phase 11KV 200A Tilting Type gang operated Load Break (16A) AB Switches with Polymer type and assembly at destination stores for use on the Distribution Transformers, Lines as per particulars given in the schedule attached.

It is not the intent to specify completely herein all the details of design and construction of Polymer Air Break Switches. However, Polymer AB Switches will confirm in all respects to high standards of engineering design and workmanship and shall be capable of performing in continuous Commercial operation up to the supplier’s guarantee, in a manner acceptable to the purchaser, who will interpret the meanings of drawings and specifications and shall have the power to reject any material, which in his judgment i.e. not in accordance with the specifications/drawings. The Polymer AB Switches offered shall be complete with all components necessary for its effective and trouble-free operation along with associated equipment etc. such components shall be deemed to be within the scope of supplier’s supply, irrespective of whether those are specifically brought out in the specification and/or in order or not. Also similar parts particularly removable ones shall be inter-changeable.

2.  STANDARDS: - The switches shall conform in all respects to the

a. IS 9920 (Part 1 to 4)/1981 with latest Amendment if any.

b. IS 2633/1986 with latest amendment if any.

c. IS 2544/1973 with latest amendment if any.

d. IEC 61109 with latest amendment if any.

e. IEC 60071 with latest amendment if any.

f.  IEC 61952 with latest amendment if any.

g. IEC 62217 with latest amendment if any.

h. IEC 60815 with latest amendment if any.

i. IS: 14255/95 with latest amendment if any.

j. IS: 8130/84 with latest amendment if any.

k. IS: 398 (Part-IV)/1994 with latest amendment if any.

3.  CLIMATE CONDITIONS: AB switches to be supplied against this specification shall be suitable for satisfactory continuous operations under following tropical conditions.

- Maximum ambient air temperature (in shade)		: 45oC

- Maximum ambient air temperature (under sun)		: 50oC

- Maximum daily average ambient air temperature	: 35oC

- Maximum yearly average ambient air temperature	: 30oC

- Maximum humidity						: 100%

- Altitude above M.S.L						: up to 1000 m

- Average No. of thunder storm days per annum		: 50

- Average No. of dust storm days per annum		: Occasional

- Average No. of rainy days/annum				: 90

- Average annual rainfall					: 925 mm

- Normal tropical monsoon period				: 4 months

- Maximum wind pressure					: 150 kg/sq.m

4.   RATINGS :

a) 	Number of Poles					:	3

b)	Nominal System Voltage 				:	11kV

b)	Rated Voltage 					:	12 kV

d)	Rated impulse withstand Voltage			:	75 kV

e)	Rated frequency					:	50 Hz.

f)	Rated Current 					:	200 A

g)	Rated peak short circuit current			:	40 kA

h)	Rated short time current 				:	16 kA

i)	Rated maximum duration of short circuit		:	1 Second.

5.   LIMITS OF TEMPERATURE RISE:

The limits of Temperature rise shall be as given in Table-4 of IS:1818/1972 and the reference conditions mentioned  therein.

The limits of Temperature rise shall be as per standards mentioned at Clause No. 8.2 of technical specification and the reference conditions mentioned therein.

6. CONSTRUCTION: (11 KV 200 A TILTING TYPE LOAD BREAK AB SWITCHES):

The Polymer A.B. Switches shall have triple pole construction as per enclosed Drawing   Nos. 1 to 4 and shall be suitable for vertical mounting. For11 KV Polymer A.B. Switch, there shall be two 11 KV Polymeric Insulator having 320 mm Creepage Distance mounted on 75 X 40 M.S. Channels per phase respectively. The channel support shall be mounted on a steel frame made of two channel supports. The switch shall be manually operated with a locking type arrangement through a hollow Square pipe coupling of 25x25 sqmm shaft and G.I. operating Pipe of 5.8 m length.

The material of the fixed contact, moving contact and jumper pad shall be electrolytic hard drawn copper (with min 99.5%) heavily nickel coated

11KV Polymeric Insulators to be used in manufacturing of AB Switches should be confirming to IEC: 61109 / IEC 61952 /IEC 60815 and mentioned therein with latest amendment.

For 11KV Polymeric Insulators: The Bidder should submit type test reports of bought up items i.e. insulators as per IEC: 61109 /IEC 61952 /IEC 60815 along with bid.

| Sr. No. | Description of type test | Test procedure/ standard | validity | Laboratory |
| --- | --- | --- | --- | --- |
| 1. | Dry lightning impulse withstand voltage test | As per IEC 61109 : 2008 | The type test reports submitted should not be more than 5 years old from date of tender opening. | Tests should be carried out in CPRI/ERDA/ any Govt. NABL accredited laboratory. |
| 2. | Wet power frequency test |  |  |  |
| 3. | Dry power frequency test |  |  |  |
| 4. | Damage limit proof test and test of the tightness of the interface between end fittings and insulator housing/Mechanical load test |  |  |  |
| 5. | Water Diffusion test on FRP rod | As per IEC 61109 C.lno.5.4.2 |  |  |
| 6. | Radio interference test | Annexure – A of section V of the tender specification |  |  |
| 7. | Brittle fracture resistance test |  |  |  |
| 8. | Chemical composition test for silicon content |  |  |  |
| 9. | Recovery of Hydrophobicity test |  | The type test reports submitted should not be more than 3 years old from date of tender opening. | Tests should be carried out either in CPRI/ERDA/ Any Govt. Labs |

6.1 The size of Composite Post insulator, minimum creepage distance and mechanical strength along with hardware fittings shall be as follows: -

| Sr. No. | Type of composite insulators | Nominal System voltage kV (rms) | Highest System voltage kV(rms) | Visible discharge test voltage kV(rms) | Wet Power Frequency Withstand voltage kV(rms) | Impulse Withstand voltage kV(rms) | Minimum Creepage Distance (mm) | Min. bending load (kN) | Minimum FRP Rod Dia(mm) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Post Insulator | 11 | 12 | 9 | 35 | 75 | 320 | 5 | 24 |

The polymeric post type insulators should be purchased from reputed manufacturers who have supplied to power distribution utilities. The bidder should submit the proof of performance certificate of original Manufacturer.

6.2	Male and female contacts shall be prepared from hard drawn copper strip. The minimum copper % shall be 99.50%

Further the contact should be nickel plated with thickness of coating not less than 10 Micron. The arcing horn shall be made of galvanized rod of 8 mm diameter. The speed of breaking of load current shall be independent of the speed of operation.

The male and female contacts from electrolytic copper will have to be mounted on polymer post type insulators with support of 40x3 mm MS HDG flat brackets. The arcing horn of fixed and moving contact should be made in such a way that they make contact before the male female contact make the contact and should part only after the male and female contact have completely separated while switching off operation.

The surface of the contact shall be rounded smooth and nickel plated. In nut shell the male and female contacts assemblies shall ensure.

- Electrodynamics withstands ability during short circuits without any risk of repulsion of contacts.

- Thermal withstands ability during short circuits.

- Constant contact pressure even when the lower parts of the insulators stacks are subjected to tensile stresses  due  to  linear  expansion of  connected  bus  bar  of  flexible  conductors  either because of temperature variations or strong winds.

- Wiping action during closing and opening.

- Fault alignment assuring closing of the switch without minute adjustments.

6.3 The spacing between the phases shall be 600 mm for 11 KV switch. Total length of square coupling rod shall be 25  x  25 x  1400 mm for 11 KV class duly hot dip galvanized as per  IS: 2633 / 1986.

6.4 The vertical operation pipe shall comprise of 25 mm (nominal bore) GI Pipe B-Class (medium class) as per IS : 1239/1979.  Length of the operating pipe shall be 5800 mm.

6.5 Suitable arrangement shall be provided to pad-lock the operating handle in “ON” and “OFF” positions.  The position of the operating handle shall be downwards when the switch is in open position and suitable guides (2 Nos.) shall be made out of HDG M.S. angle flat and supplied along with Bolts & Nuts and ferule for sliding vertical operating pipe.

6.6 The Switch outgoing terminal shall be provided with 2 mtr long 25 sqmm multi strand Aluminium AB cable wounding coil model of 30 mm ID with either side pin type 10 mm crimped lugs for each phase. The AB Cable shall be as per IS : 14255/95, IS: 8130/84 & IS: 398 (Part-IV)/1994.

The AB Cable should be purchased from reputed manufacturers who have supplied to power distribution utilities; the bidder should submit the proof of performance certificate of original Manufacture.

6.7	All iron parts shall be hot dip galvanized. The pipe shall be galvanized in accordance with IS 4736/19769.

6.8	The fixed contacts shall be of Hard Drawn Electrolytic Copper of size 40x3x190 mm 2 Nos. and capable of carrying the short circuit current of minimum 16 KA and also capable of carrying rated normal current of the switch continuously with large margin of safety at all times. The contacts should be spring loaded with stainless steel springs to maintain constant contacts pressure.

6.9	Moving contact should be made of Hard Drawn Electrolytic Copper of size 30x6x240 mm with two 10 mm holes 40 mm spacing for fixing tail clamp.

The moving contacts and the fixed contacts have to be of size and shape as shown in the diagrams attached.  The contact should be nickel plated.

6.10	Both fixed and moving contacts shall be capable of breaking load current of  16 Amps and they shall be fixed with HDG nuts & bolts.

6.11 Suitable arrangement should be provided to pad-lock the operating handle in “ON” and “OFF” position.

6.12 All ferrous parts, Bolts, Nuts, Washers etc. should be hot dip galvanized. The square pipe and GI Pipe shall also be hot dip galvanized in accordance with the IS: 2633 with latest amendment, if any.

6.13 The moving contact arrangement i.e. flower shall be provided with two 10 mm thickness brass bushes along with shaft and with a stopper bolt on the phase channel.

6.14 The Switch shall be provided with (2 Nos. tail clamp for each phase total 6 Nos.) palm type terminal connector made of Aluminium Alloy LM6 material suitable for 55 sq.mm conductor with bimetallic Plate of the same size of the contacts on which they are fixed.

6.15 The Polymeric insulators shall be mounted on a tilting base, which shall be made of cast metal with smooth surface. The supplier has to make suitable arrangement for fixing the hollow square pipe and connector of vertical rod for smooth and trouble-free operation.

7. SILICONE RUBBER POST INSULATORS

- All insulators provided shall conform to the relevant standard specifications.

- Composite insulators shed and sheath shall be made of High Temperature Vulcanizing (HTV) type silicone rubber having silicone polymer content by weight 43% minimum.

- The sheath and shell shall have excellent Hydrophobic and anti-tracking properties.

- The composite polymer weather sheds made via injection molded and shall be free from imperfections, dust and air bubble etc. It should protect the FRP rod against environmental influences, external pollution and humidity.

- The strength of the weather shed to sheath interface shall be greater than the tearing strength of the polymer.

- The FRP rods used for insulator shall be of glass-fiber reinforced epoxy resin rod of high strength (FRP rod)

- Glass fibers shall be Boron free electrically corrosion resistant (ECR) glass fiber (minimum 80%) and shall exhibit both high electrical integrity and high resistance to acid corrosion.

- Glass fibers and resin shall be optimized in the FRP rod.

- The end fitting transmit the mechanical load to the core. They shall be made of spheroidal graphite cast iron, malleable cast iron or forge steel or aluminum alloy.

- Metal end fitting shall be suitable for hardware support of respective specified mechanical load and shall be hot dip galvanized with average minimum of 115 micron and no value less than 90 micron in accordance with IS 2629. They shall be connected to the rod by means of controlled compression technique.

- The OD of end fittings should be machined to make the surface uniform round to ensure effective sealing when housing is molded over it. The material used in fittings shall be corrosion resistant.

- The post insulator shall be homogenous and free from all the cavities and flaws.

- Design of insulators shall ensued ample insulation, mechanical strength and rigidity for satisfactory operation under site conditions.

- The design shall also ensure that the losses caused by capacitive current or conduction through dielectric are minimum and that the leakage due to moist and dirty insulators surfaces I least.

- All metal caps and supports shall be crimped to the FRP rod.

#### 8.0 TYPE TEST on 11KV 200A (TT) GANG OPERATED LOAD BREAK AB SWITCHES:-

The firm should submit the following type test certificates conducted on complete isolators and their operating devices along with the certified copy of the drawing and validity should not be older than 10 years from the date of opening of tender.

- Test to prove capability of rated peak short circuit current and the rated short time current. The rated short time current should correspond to minimum of 16KA and the peak short circuit current should correspond to minimum of 40KA.

- Lightning impulse voltage test with positive & negative polarity.

- Power Frequency voltage dry test and wet test

- Temperature rise test.

- Mill volt drop tests, measurement of resistance

- Operation test.

- Mechanical endurance test.

NOTE :

(1)	All the above tests shall be conducted as per the relevant IS specification and the Bidders should compulsorily submit the above Type test Certificates along with the bid. All the above tests shall be conducted in a CPRI/ERDA or any Govt. NABL accredited labs.

(2)	For bought up items (insulators) the type test reports (as per clause 6) should be submitted compulsorily along with bid from whom the bidders are purchasing the insulators.

(3)	The bidder should submit copper percentage certificate of moving contact, fixed contact, jumper pad and aluminium & silicon composition of tail clamp from the original manufacturers along with the bid.

#### 8.1		ROUTINE TEST

The following routine test as outlined in clause No.4 of IS: 9920 (Part-4/1985) shall be carried out by the manufacturer on each unit to check certain essential requirements.

    - Power frequency voltage dry tests.

    - Measurement of the resistance of the main circuit.

    - Test to prove satisfactory operation.

#### 8.2 ACCEPTANCE TESTS:

The following acceptance test should be carried out as per IS: 9920 (P- 4/1985) on number of samples selected from the offered lot.

- Visual Inspection.

- Checking of Dimensions (of all parts as per the approved drawing).

- Power frequency voltage dry test in accordance with Cl. No.4.1 of IS- 9920-4.

- Measurement of the resistance of the main circuit in accordance with Cl.4.2of IS: 9920 (P-4).

- Test to prove satisfactory operation in accordance with Cl. No.4.3 of IS:9920-4.

- Galvanizing test as per IS: 2633.

- Temperature rise test in accordance with Cl.3.2 of IS: 9920 (Part-4) (only on one set of sample for each lot).

The temperature rise shall not exceed the maximum limit specified. The Switch shall be mounted approximately under the usual service conditions and shall be protected against undue heating or cooling. The test shall be made with the rated current of 200 Amps for the switch and the rated frequency of 50 cycles. The test shall be made for a period of time sufficient for temperature rise to reach a constant value (variation not to exceed 1degreeC per hour). The temperature shall be measured by means of thermocouples only. The temperature rise measured with the above test shall not exceed, maximum, limits specified under: -

| #### Sr. No. | #### Name of Part | #### Temperature rise limit at an ambient temperature not exceeding in C |
| --- | --- | --- |
| #### 1 | #### Nickel plated copper contacts | #### 65 ºC |
| #### 2 | #### Terminal of switches intended to be connected by external conductors by screw or bolt | #### 65 ºC |

9. Dimension of 11 Polymer AB Switches: -

As per manufacturers design subject to fulfillment of technical requirement given in this specification.

9.1 CONNECTORS :

The Aluminium connectors shall be made of Aluminium alloy with LM6 grade percentage of Aluminium shall be 83 to 85% and percentage of silicon shall be 10 to 13%. The connector should be suitable for 55 sqmm conductor for 11KV AB Switches.

9.2	MECHANICAL STRENGTH:

The isolating switches shall be capable for withstanding the rated mechanical terminal loads and electromagnetic forces, without effecting the operation and current carrying properties. The switches, complete with the operating mechanism should not come out of their own in closed position due to the effect of gravity, wind pressure, vibrations and reasonable shocks.  Their construction should be such that they do not open under the influence of the short circuit current.

9.3	LOCKING ARRANGEMENTS:

The AB (Air Break) switches shall be constructed in such a manner to permit pad locking in both open and close position.

10.	SUPPLY OF AB SWITCHES WITH POST TYPE (Polymer Insulator)

10.1.	The insulators for the isolating switches shall be of Polymer type and shall be in accordance with latest version and relevant IS (IEC: 61109). The assembly of the metal parts and polymer shall be in such a manner that the metal and polymer part shall not have any deteriorating effect or create undue stresses adversely affecting the mechanical and electrical strength of the unit arising out from any harmful expansion.  The insulators shall be of standard make.

  - Composite Insulators long rod type for tension locations and pin / post type for suspension locations

    - The insulators shall be suitable for 3Ph. 50Hz, effectively earthed 11KV O/H distribution system in a moderately/heavily polluted atmosphere.

    - Insulator manufacturer must be an indigenous manufacturer and supplier of composite insulators of rating 11KV or above or must have developed proven in house technology and manufacturing process for composite insulators of above rating OR posses technical collaboration / association with a manufacturer of composite insulators of rating 11KV or above. The Bidder shall furnish necessary evidence in support of the above along with the bid, which can be in the form of certification from the utilities concerned, or any other documents to the satisfaction of the owner.

    - Insulators shall have sheds with good self-cleaning properties. Insulator shed profile, spacing, projection etc., and selection in respect of polluted conditions shall be generally in accordance with the recommendation of IEC-60815 / IS : 13134.

    - Creepage distance shall be minimum 320 mm.

  - Interchangeability

The composite insulators including the end fitting connection shall be standard design suitable for use with the hardware fittings of any make conforming to relevant IEC/IS standards.

  - Corona and RI performance

All surfaces shall be clean, smooth, without cuts, abrasions or projections. No part shall be subjected to excessive localized pressure. The insulator and metal parts shall be so designed and manufactured that it shall avoid local corona formation and not generate any radio interference beyond specified limit under the operating conditions.

10.2 The composite insulators including the end fitting connection shall be standard design of any make conforming to relevant IEC/IS standards.

10.3 All surfaces shall be clean, smooth, without cuts, abrasions or projections. No part shall be subjected to excessive localized pressure. The insulator and metal parts shall be so designed and manufactured that it shall avoid local corona formation and not generate any radio interference beyond specified limit under the operating conditions.

11.  	SAMPLES :

One complete assembled set of 11KV 200A (TT) Gang Operated Load Break AB Switch with Post Type Polymer Insulators shall accompany the tender. However, if samples are not received along with the tender, such tenders are liable for rejection.

All AB switch samples will be examined for physical dimensional features along with weight as per specification and drawing.

The fixed contact, moving contact and jumper pad shall be electrolytic hard drawn copper (with min 99.5%) heavily nickel coated.

The tail clamp of smooth finish with buffing shall be of LM6 grade with aluminium 83 to 85% and silicon 10 to 13%

Later, one set contacts and tail clamp of the submitted sample AB Switch will be sent for NABL testing (lab will be selected by TGSPDCL) and the cost of testing shall be borne by respective bidders. The bidder shall furnish testing charges for an amount of Rs. 5,000/- (inclusive of GST) approximately in the form of Demand Draft in the name of Pay Officer, TGSPDCL, Hyderabad along with bid.

- Moving contact, fixing contact, jumper pad (one piece each) for copper % testing for confirmation of min percentage of copper (with min 99.5%) for finalization of tender.

- One no. aluminium tail clamp for aluminium and silicon % testing for confirmation of percentage of aluminium (83 to 85%) and silicon (10 to 13%) for finalization of tender.

NOTE :

- Details of parts of AB Switches shall be indicated wherever necessary in the drawings that are to be enclosed to the tender.

- Sample shall be submitted on or before due date of Tender opening by        17:00 Hrs at City-Hyd stores of TGSPDCL located at GTS Colony, Erragadda, Hyderabad.

12	Marking :

- The A. B. Switch shall be mounted with an aluminium anodized nameplate size 75x40 mm to be fixed on bottom support channels of AB Switches with rivet. Property of “TGSPDCL, Hyderabad” should be printed on name plate. It shall carry the following information duly punched or engraved on it manufacturer’s name, PO No. and date, Rated voltage, Rated normal current, rated frequency Sr. No. of A. B. Switch, etc.

- The name plate shall be weather and corrosion proof. The name plate should be fitted so that it is clearly visible as per clause 12 (i).

13.  	INSPECTION :

All routine tests and inspection shall be made at the place of manufacturer unless otherwise specially agreed upon by the manufacturer and purchaser at the time of purchase. The manufacturer shall afford the inspector representing the purchaser all reasonable facilities, without charge, to satisfy him that the material is being furnished in accordance with this specification.

The purchaser has the right to have the tests carried out at suppliers cost by an independent agency wherever there is a dispute regarding the quality of supply.

14.	Sample Procedure at Manufacturer Premises during pre-dispatch inspection:

One sample (i.e. one set) from each 50 sets or part of it to be selected at random from offered lot carrying out all acceptance tests mentioned above, except for temperature rise test, which is to be carried out only on 1 sample (i.e. on one set) from the offered lot.

For the offered lot, the supplier will have to submit type test, acceptance & routine test certificate received from the original manufacturers for the polymer insulators used in the manufacture of AB Switches. It is preferred that insulators of same make are used in one lot. However, if insulators of different make are used in one lot of AB Switch, then the supplier will have to submit type test, acceptance & routine test certificates received from the respective original manufacturers for the insulators used in AB Switches.

The supplier will have to submit chemical composition certificate from the original manufacturers for the contacts used in AB Switches for every lot.

15. 	PACKING :

The air-break switches shall be delivered suitably packed.  Although the method of packing is left to the discretion of the manufacturer, it should be robust for rough handling, that is occasioned during transportation by rail/road.

16.  	DISPATCHES:

16.1	After receipt of material at the destination stores, for every 1000 Nos. AB Switches,

Physical Dimensional inspection

- 20 Nos. AB Switches parts i.e. 1) Fixed contact 2) Moving contact 3) Jumper pad 4) Support channels 5) Insulators 6) Tail clamps 7) operating pipe 8) operating handle 9) Guides 10) AB Cable jumper etc., will be inspected for all dimensional requirements along with weights as per the specification and drawing by DE/Tech of concerned store and any DE as nominated by Corporate office.

If any of the above selected samples fails to meet the requirement as per specification and drawing, total lot will be rejected and the supplier should       re-offer the material for inspection.

Copper, Aluminium and Silicon tests:

On passing of physical verification of above samples for all dimensional requirements, samples will be picked up for testing percentage of copper, aluminium, silicon as below.

- For Moving Contact, Fixing Contact, Jumper Pad

- Samples of moving contact, fixing contact, jumper pad (each item twenty nos. from above physically verified samples) shall be sent for percentage of copper testing in any of the NABL accredited lab and such samples shall be picked up and sealed by above nominated officers in the presence of supplier representative, such testing expenditure shall borne by supplier.

- For Tail clamp:

- Samples of aluminium Tail Clamp (twenty nos. from above physically verified samples) shall be sent for testing for percentage of aluminium and silicon in any of the NABL accredited lab and such samples shall be picked up and sealed by above nominated officers in the presence of supplier representative, such testing expenditure shall borne by supplier.

- Testing charges (approximately Rs. 1,00,000/- for above samples) will be informed at the time of dispatch instructions.

All samples should meet the copper, aluminium and silicon requirement as mentioned in para 11.

16.2	If, even one contact or tail clamp of the respective sample fails in the test or the material otherwise found defective, supplier shall replace entire DI quantity which has failed in the above sample testing materials at the destination concerned on receipt of intimation from company within 30 days of such detection at his cost inclusive of to & fro transportation.

16.3	On receipt of replaced lot, again the sampling and testing procedure will be done for this material.

16.4	In the event of consecutive sample failure in lab testing of same lot, such firm’s purchase orders will be cancelled, 10% performance security will be forfeited and  firm participation in future tenders for same material will be barred for a period of one year.

Note: 	The supplier should supply extra 20 nos. of fixed contact, moving contact, jumper pad and tail clamp over and above quantity suitable for every 1000 Nos. AB Switches for sample testing. After testing, the samples will be returned to the suppliers.

17. 	DRAWING:

Two sets of detailed dimensional drawings of each part (Including Fixed and Moving Contacts) of the complete air break switches along with operating instructions shall have to be submitted along with tender.

18. 	GUARANTEED TECHNICAL PARTICULARS:

The Guaranteed Technical Particulars of the air break switches along with insulators shall be given by the bidder as per Annexure - B1& B2

19. 	THE SCHEDULE OF REQUIREMENT, DESIRED DELIVERY AND PRICES:

19.1   The Schedule of requirements and desired deliveries are indicated in Section-IV

19.2   The Schedule of prices shall be indicated online in e-procurement.

20.	GENERAL:

  - TGSPDCL reserves the right to make purchase only according to this specification.

  - A fully dimensioned sketch showing the full details of gang operation, fixed and moving contacts should necessarily accompany the tender.

  - A neat dimensioned sketch showing the details of the switch should accompany the tender.

ANNEXURE – A

Tests on Insulator units :

1. RIV Test (Dry) :

The insulator string along with complete hardware fittings shall have a radio interference voltage level below 100 micro volts at one MHz when subjected to       50 Hz A.C. voltage of 10KV & 30KV for 11KV class insulators respectively under dry condition. The test procedure shall be in accordance with the IS:8263/IEC : 437/CISPR18-2.

2. Brittle Fracture Resistance Test

Brittle fracture test shall be carried out on naked rod along with end fittings by applying “In HNO3 acid” (63 g. conc.HNO3 added to 937 g water) to the rod. The rod should be held at 80% of SML for the duration of the test. The rod should not fail within the 96-hour test duration. Test arrangement should ensure continuous wetting of the rod with Nitric acid.

3. Recovery of Hydrophobicity & Corona test

The test shall be carried out on 4mm thick samples of 5cm X 7 cm.

      - The surface of selected samples shall be cleaned with isopropyl alcohol. Allow the surface to dry and spray with water. Record the Hydrophobicity classification in line with STRI guide for Hydrophobicity classification. Dry the samples surface.

      - The sample shall be subjected to mechanical stress by bending the sample over a ground electrode. Corona is continuously generated by applying 12KV to a needle like electrode placed 1mm above the sample surface. The test shall be done for 100 hrs.

      - Immediately after the corona treatment, spray the surface with water and record the HC classification. Dry the surface and repeat the corona treatment as at clause 2 above. Note HC classification. Repeat the cycle for 1000 hrs. or unitl an HC of 6 or 7 is obtained. Dry the sample surface.

      - Allow the sample to recover and repeat hydrophobicity measurement at several time intervals. Silicone rubber should recover to HC1-HC2 within 24 to 48 hours, depending on the material and the intensity of the corona treatment.

4. 	Chemical composition test for silicon content

The content of silicon in the composite polymer shall be evaluated by EDX (Energy Dispersion X-ray) Analysis or Thermo-gravimetric analysis.

ANNEXURE – B (1)

GUARANTEED TECHNICAL PARTICULARS FOR GANG OPERATED LOAD BREAK AIR BREAK SWITCHES

| Sl. No. | Details | Guaranteed Technical Particulars |
| --- | --- | --- |
| 1. | 11 KV Outdoor type Air Break switch shall confirming IS: 9920/1981 (part-I to IV), IS: 2633 & IS: 2544/1973 with latest amendment if any and as per drawing. |  |
| a. | Name of manufacturer. |  |
| b. | Whether single break or double break. |  |
| c. | No. of Poles. |  |
| d. | Frequency. |  |
| e. | Voltage rating |  |
| f. | Current rating in Amps. i) Normal. ii) Maximum |  |
| g. | Temperature rise of the following at full rated current in O.C over ambient temperature. i) Copper contacts with coating. ii) Terminals of switches intended to be bolted to the external conductors. iii) Metallic parts acting as springs. |  |
| h. | Whether contacts are nickel coated along with thickness of coating in mm. |  |
| i. | Voltage drop across terminals of poles. |  |
| j. | Short-time current and duration & Rated Peak Withstand current |  |
| k. | Material of fixed contact. |  |
| l. | Material of moving blade. |  |
| m. | Current density & Current carrying of fixed contact & moving contact - 2A/Sq.mm & 200A |  |
| n. | Terminal connector Material : LM6 Current density & Current carrying -: 1.6A/Sq.mm & 200A |  |
| o. | Type, diameter, length & weight of operating handle. |  |
| p. | (i) Material, dia(mm) of fixed arcing horns Current carrying capacity - 10 Amp. |  |
|  | (ii) Material, dia(mm) of moving arcing horns. Current carrying capacity - 10 Amp. |  |
| q | (i) Size and length of Phase fixing channel. |  |
|  | (ii) ) Size and length of base channel. |  |
|  | (iii) XLPE Aluminium 25 sq.mm AB cable wounding coil model (30 mm ID) of 2 Mtrs. length with either side pin type 10 mm lugs |  |
| r. | Whether the Air-break switch is complete with all accessories. |  |
| s. | Whether dimensional drawing is enclosed |  |
| t. | Minimum clearance between phases (The centre distance between the insulators of adjacent phases in the assembled position of switch). |  |
| u. | Centre to Centre distance between insulators of the consecutive poles of the same phase in the assembled position of switch (in mm). |  |
| v. | Whether mechanical interlock has to be provided for arcing switches. |  |
| w. | Impulse withstand voltage with 1/50 Ms wave positive and negative polarity. i) Across isolating distance. ii) To earth and between poles. |  |
| x. | One minute power frequency withstand voltage (RMS) across Isolating distance to earth and between poles i) To earth between poles ii) Across Isolating Distance |  |

ANNEXURE – B (2)

Guaranteed technical particulars of 11KV Polymer Insulator

| Sl. No. | Description | Unit | 11KV 45KN |
| --- | --- | --- | --- |
| 1. | Type of insulators |  |  |
| 2 | Standard according to which the insulators manufactured and tested |  |  |
| 3. | Name of material used in manufacture of the insulator with class/grade) |  |  |
|  | a) Material of core (FRP rod) i) E-glass or ECR-glass ii) Boron content |  |  |
| b) | Material of housing & weather sheds (silicon content by weight) |  |  |
| c) | Material of end fittings |  |  |
| d) | Sealing compound for end fittings |  |  |
| 4 | Colour |  |  |
| 5 | Electrical characteristics : |  |  |
| a) | Nominal system voltage | kV(rms) |  |
| b) | Highest system voltage | kV(rms) |  |
| c) | Dry Power frequency withstand voltage | kV(rms) |  |
| d) | Wet power frequency withstand voltage | kV(rms) |  |
| e) | Dry flashover voltage | kV(rms) |  |
| f) | Wet flash over voltage | kV(rms) |  |
| g) | Dry lighting impulse withstand voltage a) Positive b) Negative | kV(peak) kV(peak) |  |
| h) | Dry lighting impulse flashover voltage a) Positive b) Negative | kV(peak) kV(peak) |  |
| i) | RIV at 1 MHz when energized at 10KV/30KV (rms) under dry condition | Microvolt |  |
| j) | Creepage distance (Min.) | mm |  |
| 6 | Mechanical characteristics : |  |  |
| a) | Minimum failing load | 5 KN |  |
| 7 | Dimensions of insulator |  |  |
|  | i) Weight (kg) & Height (mm) |  |  |
|  | ii) Dia. Of FRP rod | mm |  |
|  | iii) Length of FRP rod | mm |  |
|  | iv) Dia. of weathersheds | mm |  |
|  | v) Thickness of housing | mm |  |
|  | vi) Dry arc distance | mm |  |
|  | Dimensioned drawings of insulator (including weight with tolerances in weight) enclosed | Yes/No |  |
| 8 | Method of fixing of sheds to housing (specify) : Single mould or modular construction (injection moulding/compression moulding) |  |  |
| 9 | No. of weathersheds |  |  |
| 10 | Type of sheds |  |  |
| i) | Aerodynamic |  |  |
| ii) | With underribs |  |  |
| 11 | Packing details |  |  |
|  | a) Type of packing |  |  |
|  | b) No. of insulators in each pack |  |  |
|  | c) Gross weight of package |  |  |
| 12 | Any other particulars which the bidder may like go give |  |  |

| Sl. No. | Description | Size | Material | Qty. |
| --- | --- | --- | --- | --- |
| 1 | Phase fixing channel 7.14 kg/m | 75x40 mm : 1400 mm | MS HDG channel | 2 Nos. |
| 2 | Base channel 7.14 kg/m | 75x40 mm : 430 mm | MS HDG channel | 3 Nos. |
| 3 | Phase coupler pipe | 25x25x2.5 mm square 1400 mm long | MS HDG square Pipe | 1 No. |
| 4 | Solid core post type insulators | Any standard make | Polymer type | 6 Nos. |
| 5 | AB cable with either side pin type 10 mm lugs | 2 Mts. AB cable wounding coil model 30 mm ID | XLPE Aluminium 25 sq.mm AB cable | 3 Nos. |
| 6 | Moving arcing horn | 8 mm dia | MS HDG | 3 Nos. |
| 7 | Terminal connector (Tail Clamp) | Suitable for 55 sq.mm conductor as per drawing | Aluminium alloy | 6 Nos. |
| 8 | Fixed arcing horn | 8 mm Dia | MS HDG | 3 Nos. |
| 9 | Fixed contact with SS springs both sides riveted | 2x(40x3x190) mm | HDEC Cu. Flat | 3 Nos. |
| 10 | Jumper pad (fixed) | 30x6x110 mm long | HDEC Cu. Flat | 3 Nos. |
| 11 | Moving contact blade | 30x6x240 mm with two 10 mm holes 40 mm spacing for fixing tail clamp described in item no. 7 | HDEC Cu. Flat | 3 Nos. |
| 12 | Guides | 40x40x5 mm | MS HDG Angle | 2 Nos. |
| 13 | Down operating pipe | 25 Dia : 5800 mm long Weight 14.15 kgs Tolerance: + not limited -10% | GI Pipe class – B | 1 No. |
| 14 | Top operating mechanism |  | MS HDG | 1 No. |
| 15 | Bottom operating mechanism |  | MS HDG | 1 No. |
| 16 | Flower with brass bush along with 10 mm dia shaft & stopper bolt | 80x3x310 mm long 10 mm thick bush | MS HDG Brass | 3 Nos. 6 Nos. |
| 17 | Locking arrangement |  | MS HDG | 1 No. |
| 18 | Phase coupler pipe locking arrangement | 25x3x60 mm long | MS HDG | 6 Nos. |
| 19 | Moving contact fixing flat | 40x3x125 mm long | MS HDG | 6 Nos. |
| 20 | Fixed contact fixing flat | 40x3x150 mm long | MS HDG | 6 Nos. |
| - ALL FERROUS PARTS ARE HOT DIP GALVANISED. - ALL NON FERROUS CONTACT POINTS ARE NICKEL PLATED. - THE POSITION OF THE OPERATING HANDLE SHALL BE DOWNWARD WHEN THE SWITCH IS IN OPEN POSITON. - STANDARD BOLTS AND NUTS SHALL BE USED. ALL BOLTS AND NUTS SHALL BE HDG. - MS HDG: MILD STEEL HOT DIP GALVANISED HDEC : HARD DRAWN ELECTROLYTIC COPPER GI : GALVANISED IRON Al : ALUMINIUM - Dimensional Tolerance : All MS parts ±5%, : Non MS parts, Al, Cu ±2% |  |  |  |  |

Drawing-1 : Assembled AB SWITCH

Drawing - 2

TAIL CLAMP SUITABLE FOR 55 SQMM CONDUCTOR

TAIL CLAMP SUITABLE FOR 55 Sq.mm CONDUCTOR

- Clamp contact surface should be smooth finished duly buffing and maintain conforming to designation LM6 of IS: 617 (latest edition), IS:5561-1970.

DIMENSIONS:

- Tail clamp of size 130 x 50 x 12 mm.

- Pad size 75 X 30 X 12 mm Two holes on pad spaced 40 mm,

- Six hot dip galvanized bolts of 3/8" dia x 21/2 " length and double nuts with a 2 mm thick spring washer and 2 mm thick 2 flat washers for each bolt.

- Smooth finished groove suitable for 55 Sq.mm Conductor

- Two Hole Bi-metallic strip of Copper and Aluminum 70 x30 x1  mm

| Drawing – 3 : DETAILS OF FIXED AND MOVING CONTACTS Sl. No. | Item description | Size | Material |
| --- | --- | --- | --- |
| 1 | Moving arcing horn | 8 mm dia | MS HDG Rod |
| 2 | Moving contact blade | 30x6x240 mm | HDEC Copper flat |
| 3 | Moving contact fixing flat | 40x3x125 mm | MS HDG |
| 4 | MC arcing horn fixing flat | 25x3x70 mm | MS HDG |
| 5 | Fixed arcing horn | 8 dia | MS HDG Rod |
| 6 | Fixed contact | 2x(40x3x190 mm) | HDEC Copper flat (3 Nos.) |
| 7 | Supporting spring both sides metal riveted | Coil | SS wire |
| 8 | Fixed contact fixing flat | 40x3x150 mm | MS HDG |
| 9 | Jumper pad (fixed) | 30x6x110 mm | HDEC Copper flat |
| 10 | Base channel | 75x40x430 mm | MS HDG channel |
| 11 | Flower with brass bush along with 10 mm dia shaft and stopper bolt | 80x3x310 mm long 10 mm thick bush | MS HDG Rod - 3 Nos. Brass - 6 Nos. |
| 12 | Coupler pipe locking arrangement | 25x3x60 mm | MS HDG |
| 13 | Fixed contact riveted bush | - | Metal |

Drawing – 4: POLYMER POST TYPE INSULATORS GUARANTEED TECHNICAL PARAMETERS Specified Tensile Load = 5 KN Number of Sheds = 03 Dry Arcing distance = 170 mm (Min) Insulator Height = 254 mm (no tolerance) FRP Rod dia = 24 dia (Min) Normal System Voltage = 11KV Highest System Voltage = 12 KV System Frequency = 50 Hz Dry Power Frequency withstand Voltage = 45 KV Wet Power Frequency withstand Voltage = 35 KV Dry Lightning Impulse withstand Voltage = 75 KV Top & Bottom Fitting = SGI/MCI/MS Forging Applicable Standard = IEC 61109-2008 (with amendment if any

SECTION – VI

### QUALIFICATION REQUIREMENTS

1.	The bidder should be a manufacturer who must have designed, manufactured, tested and supplied to Govt. power utilities /Distribution Power utilities (inclusive private distribution power utilities) at least 40% of the quoted quantity of the goods / equipment of same or higher class indicated in the “Schedule of Requirement” in one continuous period of 12 months during the last 5 years period and its financial turnover during any one year of the last five years should have been equal or more than 100% value of the material now quoted.

At least 20% of similar material offered against this Specification should be in successful operation since 2 years as on the date of opening of the Bid with documentary evidence.  Fresh Bidders can be given order upto 15% of the total quantity as a trial order, if equipment justified.

Any company/vendor/supplier/contractor that is blacklisted/debarred by any other power utility is not eligible to participate in the tenders.

The bidders shall have to furnish an undertaking in the prescribed format (at page no.66) regarding any relation to the promoters of blacklisted / debarred companies by any utility. Any false information furnished in the declaration while rendering bid, such contract is liable for termination as well as recovery of damages.

2.	The bidder should furnish the information on all past supplies and satisfactory performance in proforma under Form 6 attested by a CA. Performance certificates issued by the purchasing authority will only be considered.

3.	The Firm should enclose a copy of GST and MSME Registration; otherwise the bid will be treated as invalid.

4.	All bids submitted will also include the following information:

i.	Copies of original documents defining the constitution or legal status, place of registration and principle place of business of the company or firm or partnership, etc.,

ii.	The bidder should furnish a brief write-up, backed with adequate data, explaining his available capacity and experience (both technical and commercial) for the manufacture and supply of the required equipment within the specified time of completion after meeting all their current commitments.

iii.	The bidder should clearly confirm that all the facilities exist in his factory for inspection and testing and these will be made available to the purchaser or his representative for inspection.

iv.	Reports on financial standing of the Bidder such as profit and loss statement, balance sheets and auditor’s report for the past five years, bankers certificates etc.

5.	The bidder will furnish Type Test Results. The type tests must have been conducted on the material offered as detailed in Technical specification as per the relevant IS in recognized laboratory as per the latest revision of the Technical Specification along with the bid.  The Bids received without type test reports will be treated as Non-Responsive.

6.	Even though the bidder meets the above qualifying criteria, they are subject to be disqualified if they have…

a.	made misleading or false representations in the forms statements and attachments submitted in proof of qualification requirements and / or

b.	record of poor performance such as not properly completing the contract, inordinate delays in supply completion, litigation history or financial failure etc.

7.	Not withstanding anything stated above the purchaser reserves the right to assess bidder’s capability and capacity to perform the contract should circumstances warrant such an assessment in the overall interest of the purchaser.

### SECTION-VII

### SAMPLE FORMS

1. BID FORM (FORM-I)

Date.  .......

TO: (Name and Address of Purchaser)

Gentlemen and/or Ladies:

Having examined the Bidding documents, the receipt of which is hereby duly acknowledged, we, the undersigned, offer to supply and deliver.  ......................... (Description of Materials / equipment) in conformity with the said bidding documents as may be ascertained in accordance with the schedule of prices (On-line Commercial stage only) and made part of this Bid.

We undertake, if our Bid is accepted, to deliver the Materials / equipment in accordance with the delivery schedule specified in the Schedule of materials.

If our Bid is accepted, we will obtain the guarantee of a bank in a sum equivalent to. 10% of the Contract Price for the due performance of the Contract, in the form prescribed by the Purchaser.

We agree to abide by this Bid upto ……………. (for the Bid Validity Period) specified in Clause and it will remain binding upon us and may be accepted at any time before the expiration of that period.

Until a formal contract is prepared and executed, this Bid, together with your written acceptance thereof and your notification of award, will constitute a binding Contract between us.

We understand that you are not bound to accept the lowest or any bid you may receive.

We certify / confirm that we comply with the eligibility requirements as per  clause  of the bidding documents.

Dated this.  ...........day of.  .............20___

____________________________

____________________________

[Signature] 					[in the capacity of]

Duly authorized to sign Bid for and on behalf of _____________________________

2. BID SECURITY FORM (FORM-II)

Whereas.  .............. (hereinafter called "the Bidder") has submitted its Bid dated (date of submission of bid) for the supply of.  ....................(name and /or description of the Materials / equipment) (hereinafter called "the Bid").

KNOW ALL PEOPLE by these presents that WE.  .............(name of bank) having our registered office at.  ...........(address of bank)(hereinafter called "the Bank"), are bound unto  ...............(name of Purchaser) (hereinafter called "the Purchaser") in the sum of …………….for which payment well and truly to be made to the said Purchaser, the Bank binds itself, its successors, and assigns by these presents. Sealed with the Common Seal of the said Bank this  ………….  day of ……………..201…..

THE CONDITIONS of this obligation are:

1.	If the Bidder

a) 	withdraws its Bid during the period of bid validity specified by the Bidder on the Bid Form; or

- does not accept the correction of errors in accordance with the Bid Specification, or

2.	If the Bidder, having been notified of the acceptance of its bid by the Purchaser during the period of bid validity;

(a)	fails or refuses to furnish the performance security, in accordance with the Bid Specification.

(b)	fails or refuses to execute the Contract Form if required; or

We undertake to pay the Purchaser up to the above amount upon receipt of its first written demand, without the Purchaser having to substantiate its demand, provided that in its demand the Purchaser will note that the amount claimed by it is due to it, owing to the occurrence of one or both of the two conditions, specifying the occurred condition or conditions.

This guarantee will remain in force up to and including forty five (45) days after …………….(Specification Date) the period of the bid validity, i.e., total for 135 days from the date of bid opening, and any demand in respect thereof should reach the Bank not later than the above date.

.  ....................

(Signature of the Bank)

NOTE:	This will be executed on a Rs.100/- non-judicial stamp paper issued by a Nationalized/Scheduled  Bank.

3. PERFORMANCE SECURITY FORM (FORM-III)

To:                        (Name of Purchaser)

WHEREAS………………………………………..(Name of Supplier)

(hereinafter called "the Supplier") has undertaken, in pursuance of Contract No.............dated.............200 to supply.  ................(Description of Materials / equipment and Services)

(hereinafter called "the Contract").

AND WHEREAS it has been stipulated by you in the said Contract that the Supplier will furnish you with a Bank Guarantee by a recognized Bank(Nationalized/Scheduled )for the sum specified therein as security for compliance with the Supplier's performance obligations in accordance with the Contract.

AND WHEREAS we have agreed to give the Supplier a Guarantee:

THEREFORE WE hereby affirm that we are Guarantors and responsible to you, on behalf of the Supplier, up to a total of.  ............................ (Amount of the Guarantee in Words and Figures) and we undertake to pay you,  upon your first written demand declaring the Supplier to be in default under the Contract and without cavil or argument, any sum or sums within the limit of................ (Amount of Guarantee) as aforesaid, without your needing to prove or to show grounds or reasons for your demand or the sum specified therein.

This guarantee is valid until the.  ... day of.  ..... 201…….

Signature and Seal of Guarantors

..........................................

Date.  .......................201…

..........................................

..........................................

Address:....................…...

..........................................

..........................................

NOTE:	This will be executed on a Rs.100/- non-judicial stamp paper by a nationalized/scheduled Bank.

4. CONTRACT FORM (FORM-IV)

THIS AGREEMENT made the.  ....... day of.  ............ 201…..  Between.  ..............(Name of Purchaser) of the one part and.  ..........(Name of Supplier) of the other part:

WHEREAS   the Purchaser invited bids for certain Materials / equipment and ancillary services viz.,

.....................(Brief description of Materials / equipment and Services) and has accepted a bid by the Supplier for the supply of those Materials / equipment and services in the sum of.  .....................(Contract Price in Words and Figures)(hereinafter called "the Contract Price").

NOW THIS AGREEMENT WITNESSETH AS FOLLOWS:

1.	In this Agreement words and expressions will have the same meanings as are respectively assigned to them in the Conditions of Contract referred to.

2.	The following documents will be deemed to form and be read and construed as part of this Agreement, viz.:

(a)	the Bid Form and the Price Schedule submitted by the  Bidder;

(b)	the Schedule of Requirements;

(c)	the Technical Specifications;

(d)	the General Conditions of Contract;

(e)	the Purchaser's Notification of Award.

3.	In consideration of the payments to be made by the Purchaser to the Supplier as hereinafter mentioned, the Supplier hereby covenants with the Purchaser to provide the Materials / equipment and services and to remedy defects therein in conformity in all respects with the provisions of the Contract.

4.	The Purchaser hereby covenants to pay the Supplier in consideration of the provision of the Materials / equipment and services and the remedying of defects therein, the Contract Price or such other sum as may become payable under the provisions of the Contract at the times and in the manner prescribed by the Contract.

Brief particulars of the Materials / equipment and services which will be supplied/ provided by the Supplier are as under:

| Sl. No. | Brief Description of Materials / Equipment & services | Quantity to be supplied | Unit Price Rs. | Total Price Rs. | Delivery Terms |
| --- | --- | --- | --- | --- | --- |

TOTAL VALUE:	(Rupees 			     	 		only)

DELIVERY SCHEDULE:

IN WITNESS whereof the parties hereto have caused this Agreement to be executed on the day and year first above written.

Signed, Sealed and Delivered by the

said.  ..............................(for the Purchaser)

in the presence of.  ................

Signed, Sealed and Delivered by the

said.  ..............................(for the Supplier)

in the presence of.  ................

NOTE:	To be executed on a Rs.100/- Non-judicial stamp paper.

5. DETAILS TO BE FURNISHED BY THE MANUFACTURER (FORM-V)

| 1. Specification No. | : |  |
| --- | --- | --- |
| 2. Name of the Material | : |  |
| 3. Quantity to be procured | : |  |
| 4. Last date and time for submission of Bid | : |  |
| 5. Date and time for opening of Bid | : |  |
| 6. State whether Bid security is enclosed | : |  |
| 7. State whether the quotation in two parts has been submitted. | : |  |
| 8. State whether 20% minimum quantity for each item is quoted, if yes mention the quoted quantity in Nos. | : |  |
| 9. Whether willing to furnish performance B.G. @ 10% if order is placed | : |  |
| 10. Indicate the month wise delivery Schedule. | : |  |
| 11. Prices whether Firm | : |  |
| 12. Whether any other GST payable. If so give details and the same is included / not included. | : |  |
| 13. State whether TGSPDCL terms of payment are accepted. | : |  |
| 14. Quantity offered for supply in Nos. | : |  |
| 15. State whether 90 days validity offered | : |  |
| 16. Whether sample is enclosed (if specified) | : |  |
| 17. Whether the material/equipment offered conforms to the relevant TGSPDCL Specification | : |  |
| 18. Whether you have executed orders of the TGSPDCL previously for these items. (Please give details) | : |  |
| 19. Similar details in respect of supplies made to other utilities | : |  |
| 20. Whether Bid security exemption letter enclosed, if exempted in case of Govt. firms. | : |  |
| 21. Whether GSTR 3B returns enclosed | : |  |
| 22. Whether Income-tax clearance certificate enclosed. | : |  |
| 23. Whether Warranty clause accepted | : |  |
| 24. Whether Penalty clause accepted | : |  |
| 25. Whether delivery schedule accepted | : |  |

Place:								Signature of the Bidder:

Date:								Name:

Business address:

6.  PROFORMA FOR PERFORMANCE STATEMENT (FORM – VI)

Bid No.__________				Date of Opening________

Time _______ Hours

Name of the Firm__________________________________________

| Order placed by (full address of purchaser) | Order No. and Date | Description and quantity of ordered equipment | Date of Completion of Delivery |  |
| --- | --- | --- | --- | --- |
|  |  |  | As per Contract | Actual |

| Remarks indicating reasons for late delivery, if any | Has the equipment been satisfactorily functioning? (Attach a Certificate from the Purchaser) |
| --- | --- |

Signature of the Bidder _______________________

________________________

________________________

7. SCHEDULE OF DEVIATION (FORM – VII)

# (i) TECHNICAL (FORM – VII (A))

| Sl. No. | Requirements / Equipment | Specification Clause No. | Deviations | Remarks |
| --- | --- | --- | --- | --- |

It is hereby conformed that except for deviations mentioned above, the offer conforms to all the other features specified in Technical Specification Section ____ of this Bid Document

Place :								Signature of the Bidder :

Date :								Name :

Business address  :

# (ii) COMMERCIAL (FORM – VII (B))

| Sl. No. | Requirements / Equipment | Specification Clause No. | Deviations | Remarks |
| --- | --- | --- | --- | --- |

It is hereby conformed that except for deviations mentioned above, the offer conforms to all the other features specified in Commercial Specification Section ____ of this Bid Document

Place :								Signature of the Bidder :

Date :								Name :

Business address:

8.	Declaration to be given by the Company in regard to relation to promoters of Blacklisted / debarred companies by any power utilities.

(FORM – VIII)

I declare that, myself or any of the representatives of my company / firm do not have any relation with promoters of blacklisted / debarred companies by any utilities.

It is certified that the information furnished above is true to the best of my knowledge and belief. It is hereby undertaken that in the event of the above information found to be false or incorrect at a later date, the TGSPDCL is entitled to terminate the contract/agreement entered into besides recovering damages as may be found necessary, with due notice.

Signature of authorized representative